## Summary
Option 3B Summary
Item | Chainage | Value
Pipeline | 0-8 | 1.9 | m - Diameter
Pump Station | 8 | 50 | m - Pumping Head
Pipeline | 8-22 | 1.9 | m - Diameter
Break Pressure | 22 | 10 | m - Elevation
Pipeline | 22-274 | 2.2 | m - Diameter
Break Pressure | 274 | 10 | m -Elevation
Pump Station | 274 | 160 | m - Pumping Head
Pipeline | 274-336 | 2.2 | m -Diameter
Pipeline | 336-478 | 1.8 | m -Diameter
Pipeline | 478-500 | 1.5 | m - Diameter

## Profile data
Longitudinal profile data - Botswana pipeline
| OPTION 1: Pipeline goes through Serule before joining to BPT1 | OPTION2: Pipeline goes directly to BPT1
CHAINAGE (km0 | NGL (m) | NGL (m) |  | Botswana 1
2 | 1069.018 | 1069.018 | Start | Botswana 2
4 | 1067.321 | 1067.321
6 | 1064.035 | 1064.035
8 | 1063.832 | 1063.832
10 | 1067.893 | 1067.893
12 | 1075.133 | 1075.133
14 | 1082.768 | 1082.768
16 | 1089.726 | 1089.726
18 | 1094.131 | 1094.131
20 | 1097.897 | 1097.897
22 | 1101.67 | 1101.67
24 | 1095.952 | 1095.952
26 | 1090.107 | 1090.107
28 | 1085.781 | 1085.781
30 | 1081.89 | 1081.89
32 | 1077.937 | 1077.937
34 | 1074.89 | 1074.89
36 | 1071.114 | 1071.114
38 | 1065.311 | 1065.311
40 | 1059.051 | 1059.051
42 | 1054.28 | 1054.28
44 | 1053.871 | 1053.871
46 | 1050.42 | 1050.42
48 | 1052.704 | 1052.704
50 | 1056.355 | 1056.355
52 | 1058.466 | 1058.466
54 | 1055.99 | 1055.99
56 | 1055.66 | 1055.66
58 | 1056.404 | 1056.404
60 | 1056.841 | 1056.841
62 | 1056.377 | 1056.377
64 | 1052.503 | 1052.503
66 | 1046.022 | 1046.022
68 | 1036.575 | 1036.575
70 | 1031.818 | 1031.818
72 | 1027.675 | 1027.675
74 | 1023.844 | 1023.844
76 | 1020.888 | 1020.888
78 | 1023.648 | 1023.648
80 | 1027.566 | 1027.566
82 | 1032.371 | 1032.371
84 | 1034.983 | 1034.983
86 | 1033.213 | 1033.213
88 | 1031.188 | 1031.188
90 | 1029.08 | 1029.08
92 | 1026.322 | 1026.322
94 | 1023.207 | 1023.207
96 | 1021.503 | 1021.503
98 | 1019.765 | 1019.765
100 | 1018.493 | 1018.493
102 | 1016.444 | 1016.444
104 | 1013.288 | 1013.288
106 | 1007.843 | 1007.843
108 | 1001.282 | 1001.282
110 | 996.609 | 996.609
112 | 992.999 | 992.999
114 | 993.639 | 993.639
116 | 994.611 | 994.611
118 | 995.751 | 995.751
120 | 996.479 | 996.479
122 | 996.147 | 996.147
124 | 992.094 | 992.094
126 | 985.623 | 985.623
128 | 977.759 | 977.759
130 | 969.772 | 969.772
132 | 981.785 | 981.785
134 | 991.458 | 991.458
136 | 987.77 | 987.77
138 | 982.725 | 982.725
140 | 977.559 | 977.559
142 | 975.289 | 975.289
144 | 973.968 | 973.968
146 | 962.473 | 962.473
148 | 951.285 | 951.285
150 | 948.174 | 948.174
152 | 944.641 | 944.641
154 | 941.566 | 941.566
156 | 940.942 | 940.942
158 | 939.726 | 939.726
160 | 936.738 | 936.738
162 | 933.65 | 933.65
164 | 932.745 | 932.745
166 | 931.696 | 931.696
168 | 930.999 | 930.999
170 | 930.885 | 930.885
172 | 930.378 | 930.378
174 | 931.324 | 931.324
176 | 933.53 | 933.53
178 | 932.714 | 932.714
180 | 928.311 | 928.311
182 | 924.179 | 924.179
184 | 928.398 | 928.398
186 | 930.866 | 930.866
188 | 928.411 | 928.411
190 | 927.849 | 927.849
192 | 926.71 | 926.71
194 | 926.201 | 926.201
196 | 924.509 | 924.509
198 | 923.417 | 923.417
200 | 923.011 | 923.011
202 | 921.969 | 921.969
204 | 920.661 | 920.661
206 | 920.243 | 920.243
208 | 919.297 | 919.297
210 | 917.533 | 917.533
212 | 917.684 | 917.684
214 | 915.724 | 915.724
216 | 915.73 | 915.73
218 | 915.584 | 915.584
220 | 915.444 | 915.444
222 | 913.52 | 913.52
224 | 912.524 | 912.524
226 | 912.565 | 912.565
228 | 913.484 | 913.484
230 | 913.545 | 913.545
232 | 914.546 | 914.546
234 | 918.285 | 918.285
236 | 919.357 | 919.357
238 | 918.649 | 918.649
240 | 922.974 | 922.974
242 | 927.375 | 927.375
244 | 929.253 | 929.253
246 | 930.863 | 930.863
248 | 931.924 | 931.924
250 | 936.722 | 936.722
252 | 941.777 | 941.777
254 | 948.143 | 948.143
256 | 955.417 | 955.417
258 | 962.7 | 962.7
260 | 969.281 | 969.281
262 | 980.284 | 980.284
264 | 986.551 | 986.551
266 | 989.198 | 989.198
268 | 994.39 | 994.39
270 | 999.917 | 999.917
272 | 1004.623 | 1004.623
274 | 1008.819 | 1008.819
276 | 1007.834 | 1007.834
278 | 1005.626 | 1005.626
280 | 1001.623 | 1001.623
282 | 1004.052 | 1004.052
284 | 1010.797 | 1010.797
286 | 1014.67 | 1014.67
288 | 1017.319 | 1017.319
290 | 1027.459 | 1027.459
292 | 1031.99 | 1031.99
294 | 1036.254 | 1036.254
296 | 1040.127 | 1040.127
298 | 1044.396 | 1044.396
300 | 1051.339 | 1051.339
302 | 1060.955 | 1060.955
304 | 1070.227 | 1070.227
306 | 1072.691 | 1072.691
308 | 1076.503 | 1076.503
310 | 1083.996 | 1083.996
312 | 1097.188 | 1097.188
314 | 1103.545 | 1103.545
316 | 1105.174 | 1105.174
318 | 1111.657 | 1111.657
320 | 1122.935 | 1122.935
322 | 1128.197 | 1128.197
324 | 1132.561 | 1132.561
326 | 1131.854 | 1131.854
328 | 1133.338 | 1133.338
330 | 1136.405 | 1136.405
332 | 1128.709 | 1128.709
334 | 1120.713 | 1120.713
336 | 1115.226 | 1115.226
338 | 1108.709 | 1108.709
340 | 1102.499 | 1102.499
342 | 1096.349 | 1096.349
344 | 1090.39 | 1090.39
346 | 1087.765 | 1087.765
348 | 1084.661 | 1084.661
350 | 1081.662 | 1081.662
352 | 1076.872 | 1076.872
354 | 1070.898 | 1070.898
356 | 1065.018 | 1065.018
358 | 1059.58 | 1059.58
360 | 1055.284 | 1055.284
362 | 1050.886 | 1050.886
364 | 1052.647 | 1052.647
366 | 1051.117 | 1051.117
368 | 1048.266 | 1048.266
370 | 1040.172 | 1040.172
372 | 1033.483 | 1033.483
374 | 1030.95 | 1030.95
376 | 1032.263 | 1032.263
378 | 1031.391 | 1031.391
380 | 1025.791 | 1025.791
382 | 1020.911 | 1020.911
384 | 1015.65 | 1015.65
386 | 1012.139 | 1012.139
388 | 1010.472 | 1010.472
390 | 1005.401 | 1005.401
392 | 996.666 | 996.666
394 | 991.35 | 991.35
396 | 990.486 | 990.486
398 | 992.761 | 992.761
400 | 999.077 | 999.077
402 | 1001.8 | 1001.8
404 | 1002.224 | 1002.224
406 | 1002.003 | 1002.003
408 | 1003.596 | 1003.596
410 | 994.111 | 994.111
412 | 983.925 | 983.925
414 | 972.347 | 972.347
416 | 963.901 | 963.901
418 | 963.258 | 963.258
420 | 965.836 | 965.872
422 | 966.309 | 966.177
424 | 972.884 | 973.825
426 | 983.972 | 983.972
428 | 994.096 | 994.096
430 | 991.695 | 991.695
432 | 984.933 | 984.933
434 | 978.185 | 974.509
436 | 972.686 | 966.698
438 | 966.824 | 963.618
440 | 960.902 | 957.803
442 | 952.924 | 954.277
444 | 945.683 | 947.182
446 | 941.042 | 938.045
448 | 937.104 | 930.871
450 | 939.943 | 926.391
452 | 944.776 | 918.344
454 | 947.762 | 911.505
456 | 952.649 | 903.61
458 | 954.554 | 900.63
460 | 952.37 | 904.066
462 | 947.552 | 915.092
464 | 941.898 | 905.556
466 | 940.521 | 905.271
468 | 939.702 | 901.918
470 | 937.147 | 895.651
472 | 933.872 | 892.304
474 | 933.184 | 895.279
476 | 939.292 | 896.818
478 | 944.619 | 909.921
480 | 954.023 | 926.295
482 | 968.263 | 924.888
484 | 970.384 | 919.044
486 | 964.636 | 911.164
488 | 956.631 | 903.893
490 | 947.426 | 901.953
492 | 941.72 | 900.198
494 | 935.985 | 904.177
496 | 930.475 | 912.253
498 | 927.611 | 915.297
500 | 931.256 | 919.629
502 | 920.044
504 | 911.78
506 | 907.989
508 | 907.289
510 | 900.577
512 | 902.112
514 | 900.179
516 | 903.811
518 | 910.027
520 | 911.131 |  | End

## Flow Rate Calculations
Estimated Transfer Rate Demand | 100 | Mm3/a
Availible Days | 365
Pumping Hours | 24
Pf | 1.052
Pl | 1.02
PR | 1.2
Peak Design Flow | 4.0831 | m3/s

## Calculation Constants
Friction Factors
Ks (mm) - New | 0.03
Ks (mm) - Average | 0.06
Ks (mm) - Old | 0.15
Ks (mm) - Biofilm | 0.5
Kinemeatic Viscosity | 1.13e-06 | m2/s
Minor Loss - k | 150
Grade of Steel | X42
Yeild Capacity | 300 | Mpa
Design % of Yeild | 50%
Minimum D/t ratio | 160 | mm/mm

## Hydraulics
Option 3B |  |  |  | Option 3B | [12 empty] | Option 3B
Pump Station |  |  |  | Pipe Line | [9 empty] | Steel Pipeline Design |  |  | New Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Average Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Old Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Biofilm Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes
Name | Chainage (km) | Elevation (m) | Pumped Head (m) | Reference | Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Flow Rate (m3/s) | PipeVelocity (m/s) | Re | Static Head (m) | Dynamic Head (m) | Design Pressure (m) | Pipe Wall thickness (mm) | Steel Mass (kg) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m)
PS 1 | 8 | 1063.832 | 50 | Reservoir | 2 | 1069.018 | 0 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 10 | 10 | 10 | 11.875 | 0 | 0.00867 |  |  | 0 | 0 | 10 | 1079.018 | 0.0097304 |  |  | 0 | 0 | 10 | 1079.018 | 0.011459 |  |  | 0 | 0 | 10 | 1079.018 | 0.014543 |  |  | 0 | 0 | 10 | 1079.018
PS2 | 274 | 1008.819 | 160 |  | 4 | 1067.321 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 11.697 | 10.6689 | 11.697 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 10.6689 | 1077.9899 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 10.5509 | 1077.8719 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 10.3586 | 1077.6796 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 10.0086 | 1077.3296
[5 empty] | 6 | 1064.035 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 14.983 | 12.9268 | 14.983 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 12.9268 | 1076.9618 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 12.6908 | 1076.7258 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 12.3062 | 1076.3412 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 11.6062 | 1075.6412
|  |  |  | Pump Station | 8 | 1063.832 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 62.1017 | 61.7477 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 50 | 62.1017 | 1125.9337 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 50 | 61.7477 | 1125.5797 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 50 | 61.1707 | 1125.0027 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 50 | 60.1208 | 1123.9528
[5 empty] | 10 | 1067.893 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 57.0126 | 56.5407 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 57.0126 | 1124.9056 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 56.5407 | 1124.4337 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 55.7713 | 1123.6643 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 54.3714 | 1122.2644
Reservoirs |  |  |  |  | 12 | 1075.133 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 48.7445 | 48.1546 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 48.7445 | 1123.8775 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 48.1546 | 1123.2876 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 47.1929 | 1122.3259 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 45.443 | 1120.576
Name | Chainage (km) | Water Elevation (m) | Height |  | 14 | 1082.768 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 40.0814 | 39.3735 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 40.0814 | 1122.8494 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 39.3735 | 1122.1415 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 38.2195 | 1120.9875 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 36.1196 | 1118.8876
Supply Resrvoir | 2 | 1079.018 | 10 |  | 16 | 1089.726 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 32.0953 | 31.2694 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 32.0953 | 1121.8213 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 31.2694 | 1120.9954 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 29.9231 | 1119.6491 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.4732 | 1117.1992
BPT 3 | 22 | 1111.67 | 10 |  | 18 | 1094.131 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 26.6622 | 25.7183 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 26.6622 | 1120.7932 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 25.7183 | 1119.8493 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 24.1796 | 1118.3106 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 21.3798 | 1115.5108
BPT 4 | 274 | 1018.819 | 10 |  | 20 | 1097.897 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 21.8681 | 20.8062 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 21.8681 | 1119.7651 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 20.8062 | 1118.7032 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 19.0752 | 1116.9722 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 15.9254 | 1113.8224
BPT 1 | 500 | 929.629 | 10 | Reservoir | 22 | 1101.67 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 10 | 10 | 10 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 10 | 1111.67 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 10 | 1111.67 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 10 | 1111.67 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 10 | 1111.67
[5 empty] | 24 | 1095.952 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 15.718 | 15.23 | 15.718 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 15.23 | 1111.182 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 15.1754 | 1111.1274 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 15.0865 | 1111.0385 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 14.926 | 1110.878
[5 empty] | 26 | 1090.107 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 21.563 | 20.5871 | 21.563 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 20.5871 | 1110.6941 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 20.4777 | 1110.5847 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 20.3 | 1110.407 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 19.9789 | 1110.0859
|  | -32.652 |  |  | 28 | 1085.781 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 25.889 | 24.4251 | 25.889 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 24.4251 | 1110.2061 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 24.2611 | 1110.0421 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 23.9945 | 1109.7755 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 23.5129 | 1109.2939
|  | 92.851 |  |  | 30 | 1081.89 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 29.78 | 27.8281 | 29.78 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 27.8281 | 1109.7181 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 27.6095 | 1109.4995 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 27.254 | 1109.144 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 26.6118 | 1108.5018
[5 empty] | 32 | 1077.937 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 33.733 | 31.2931 | 33.733 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 31.2931 | 1109.2301 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 31.0198 | 1108.9568 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 30.5755 | 1108.5125 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 29.7728 | 1107.7098
[5 empty] | 34 | 1074.89 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 36.78 | 33.8522 | 36.78 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 33.8522 | 1108.7422 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 33.5242 | 1108.4142 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 32.991 | 1107.881 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 32.0277 | 1106.9177
[5 empty] | 36 | 1071.114 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 40.556 | 37.1402 | 40.556 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 37.1402 | 1108.2542 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 36.7576 | 1107.8716 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 36.1355 | 1107.2495 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 35.0117 | 1106.1257
Route | Botswana 2 |  |  |  | 38 | 1065.311 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 46.359 | 42.4552 | 46.359 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 42.4552 | 1107.7662 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 42.018 | 1107.329 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 41.307 | 1106.618 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 40.0226 | 1105.3336
Option | 3B |  |  |  | 40 | 1059.051 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 52.619 | 48.2273 | 52.619 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 48.2273 | 1107.2783 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 47.7353 | 1106.7863 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 46.9355 | 1105.9865 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 45.4906 | 1104.5416
[5 empty] | 42 | 1054.28 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 57.39 | 52.5103 | 57.39 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 52.5103 | 1106.7903 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 51.9637 | 1106.2437 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 51.075 | 1105.355 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 49.4695 | 1103.7495
[5 empty] | 44 | 1053.871 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 57.799 | 52.4313 | 57.799 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 52.4313 | 1106.3023 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 51.8301 | 1105.7011 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 50.8525 | 1104.7235 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 49.0865 | 1102.9575
[5 empty] | 46 | 1050.42 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 61.25 | 55.3943 | 61.25 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 55.3943 | 1105.8143 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 54.7384 | 1105.1584 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 53.672 | 1104.092 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 51.7454 | 1102.1654
[5 empty] | 48 | 1052.704 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 58.966 | 52.6224 | 58.966 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 52.6224 | 1105.3264 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 51.9118 | 1104.6158 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 50.7565 | 1103.4605 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 48.6694 | 1101.3734
[5 empty] | 50 | 1056.355 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 55.315 | 48.4834 | 55.315 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 48.4834 | 1104.8384 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 47.7182 | 1104.0732 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 46.474 | 1102.829 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 44.2263 | 1100.5813
[5 empty] | 52 | 1058.466 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 53.204 | 45.8844 | 53.204 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 45.8844 | 1104.3504 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 45.0645 | 1103.5305 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 43.7315 | 1102.1975 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 41.3233 | 1099.7893
[5 empty] | 54 | 1055.99 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 55.68 | 47.8725 | 55.68 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 47.8725 | 1103.8625 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 46.9979 | 1102.9879 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 45.576 | 1101.566 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 43.0072 | 1098.9972
[5 empty] | 56 | 1055.66 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 56.01 | 47.7145 | 56.01 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 47.7145 | 1103.3745 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 46.7853 | 1102.4453 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 45.2745 | 1100.9345 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 42.5452 | 1098.2052
[5 empty] | 58 | 1056.404 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 55.266 | 46.4825 | 55.266 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 46.4825 | 1102.8865 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 45.4987 | 1101.9027 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 43.899 | 1100.303 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 41.0091 | 1097.4131
[5 empty] | 60 | 1056.841 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 54.829 | 45.5576 | 54.829 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 45.5576 | 1102.3986 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 44.519 | 1101.36 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 42.8305 | 1099.6715 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 39.7801 | 1096.6211
[5 empty] | 62 | 1056.377 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 55.293 | 45.5336 | 55.293 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 45.5336 | 1101.9106 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 44.4404 | 1100.8174 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 42.663 | 1099.04 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 39.452 | 1095.829
[5 empty] | 64 | 1052.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 59.167 | 48.9196 | 59.167 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 48.9196 | 1101.4226 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 47.7718 | 1100.2748 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 45.9055 | 1098.4085 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 42.534 | 1095.037
[5 empty] | 66 | 1046.022 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 65.648 | 54.9126 | 65.648 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 54.9126 | 1100.9346 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 53.7101 | 1099.7321 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 51.755 | 1097.777 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 48.2229 | 1094.2449
[5 empty] | 68 | 1036.575 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 75.095 | 63.8717 | 75.095 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 63.8717 | 1100.4467 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 62.6145 | 1099.1895 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 60.5705 | 1097.1455 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 56.8779 | 1093.4529
[5 empty] | 70 | 1031.818 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 79.852 | 68.1407 | 79.852 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 68.1407 | 1099.9587 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 66.8289 | 1098.6469 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 64.696 | 1096.514 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 60.8428 | 1092.6608
[5 empty] | 72 | 1027.675 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 83.995 | 71.7957 | 83.995 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 71.7957 | 1099.4707 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 70.4292 | 1098.1042 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 68.2075 | 1095.8825 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 64.1938 | 1091.8688
[5 empty] | 74 | 1023.844 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 87.826 | 75.1388 | 87.826 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 75.1388 | 1098.9828 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 73.7176 | 1097.5616 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 71.407 | 1095.251 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 67.2327 | 1091.0767
[5 empty] | 76 | 1020.888 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 90.782 | 77.6068 | 90.782 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 77.6068 | 1098.4948 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 76.131 | 1097.019 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 73.7315 | 1094.6195 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 69.3967 | 1090.2847
[5 empty] | 78 | 1023.648 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 88.022 | 74.3588 | 88.022 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 74.3588 | 1098.0068 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 72.8284 | 1096.4764 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 70.34 | 1093.988 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 65.8446 | 1089.4926
[5 empty] | 80 | 1027.566 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 84.104 | 69.9528 | 84.104 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 69.9528 | 1097.5188 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 68.3677 | 1095.9337 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 65.7905 | 1093.3565 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 61.1346 | 1088.7006
[5 empty] | 82 | 1032.371 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 79.299 | 64.6599 | 79.299 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 64.6599 | 1097.0309 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 63.0201 | 1095.3911 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 60.354 | 1092.725 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 55.5375 | 1087.9085
[5 empty] | 84 | 1034.983 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 76.687 | 61.5599 | 76.687 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 61.5599 | 1096.5429 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 59.8655 | 1094.8485 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 57.1105 | 1092.0935 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 52.1335 | 1087.1165
[5 empty] | 86 | 1033.213 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 78.457 | 62.8419 | 78.457 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 62.8419 | 1096.0549 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 61.0928 | 1094.3058 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 58.249 | 1091.462 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 53.1114 | 1086.3244
[5 empty] | 88 | 1031.188 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 80.482 | 64.379 | 80.482 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 64.379 | 1095.567 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 62.5752 | 1093.7632 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 59.6425 | 1090.8305 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 54.3444 | 1085.5324
[5 empty] | 90 | 1029.08 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 82.59 | 65.999 | 82.59 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 65.999 | 1095.079 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 64.1406 | 1093.2206 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 61.119 | 1090.199 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 55.6603 | 1084.7403
[5 empty] | 92 | 1026.322 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 85.348 | 68.269 | 85.348 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 68.269 | 1094.591 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 66.3559 | 1092.6779 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 63.2455 | 1089.5675 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 57.6263 | 1083.9483
[5 empty] | 94 | 1023.207 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 88.463 | 70.896 | 88.463 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 70.896 | 1094.103 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 68.9283 | 1092.1353 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 65.729 | 1088.936 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 59.9492 | 1083.1562
[5 empty] | 96 | 1021.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 90.167 | 72.1121 | 90.167 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 72.1121 | 1093.6151 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 70.0897 | 1091.5927 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 66.8015 | 1088.3045 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 60.8612 | 1082.3642
[5 empty] | 98 | 1019.765 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 91.905 | 73.3621 | 91.905 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 73.3621 | 1093.1271 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 71.285 | 1091.05 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 67.908 | 1087.673 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 61.8071 | 1081.5721
[5 empty] | 100 | 1018.493 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 93.177 | 74.1461 | 93.177 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 74.1461 | 1092.6391 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 72.0144 | 1090.5074 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 68.5485 | 1087.0415 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 62.2871 | 1080.7801
[5 empty] | 102 | 1016.444 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 95.226 | 75.7072 | 95.226 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 75.7072 | 1092.1512 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 73.5208 | 1089.9648 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 69.966 | 1086.41 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 63.544 | 1079.988
[5 empty] | 104 | 1013.288 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 98.382 | 78.3752 | 98.382 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 78.3752 | 1091.6632 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 76.1342 | 1089.4222 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 72.4905 | 1085.7785 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 65.908 | 1079.196
[5 empty] | 106 | 1007.843 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 103.827 | 83.3322 | 103.827 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 83.3322 | 1091.1752 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 81.0365 | 1088.8795 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 77.304 | 1085.147 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 70.5609 | 1078.4039
[5 empty] | 108 | 1001.282 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 110.388 | 89.4053 | 110.388 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 89.4053 | 1090.6873 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 87.0549 | 1088.3369 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 83.2335 | 1084.5155 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 76.3299 | 1077.6119
[5 empty] | 110 | 996.609 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 115.061 | 93.5903 | 115.061 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 93.5903 | 1090.1993 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 91.1853 | 1087.7943 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 87.275 | 1083.884 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 80.2108 | 1076.8198
[5 empty] | 112 | 992.999 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 118.671 | 96.7123 | 118.671 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 96.7123 | 1089.7113 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 94.2526 | 1087.2516 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 90.2535 | 1083.2525 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 83.0288 | 1076.0278
[5 empty] | 114 | 993.639 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 118.031 | 95.5843 | 118.031 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 95.5843 | 1089.2233 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 93.07 | 1086.709 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 88.982 | 1082.621 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 81.5967 | 1075.2357
[5 empty] | 116 | 994.611 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 117.059 | 94.1244 | 117.059 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 94.1244 | 1088.7354 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 91.5554 | 1086.1664 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 87.3785 | 1081.9895 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 79.8327 | 1074.4437
[5 empty] | 118 | 995.751 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 115.919 | 92.4964 | 115.919 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 92.4964 | 1088.2474 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 89.8727 | 1085.6237 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 85.607 | 1081.358 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 77.9006 | 1073.6516
[5 empty] | 120 | 996.479 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 115.191 | 91.2804 | 115.191 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 91.2804 | 1087.7594 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 88.6021 | 1085.0811 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 84.2475 | 1080.7265 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 76.3806 | 1072.8596
[5 empty] | 122 | 996.147 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 115.523 | 91.1245 | 115.523 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 91.1245 | 1087.2715 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 88.3915 | 1084.5385 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 83.948 | 1080.095 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 75.9205 | 1072.0675
[5 empty] | 124 | 992.094 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 119.576 | 94.6895 | 119.576 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 94.6895 | 1086.7835 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 91.9019 | 1083.9959 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 87.3695 | 1079.4635 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 79.1815 | 1071.2755
[5 empty] | 126 | 985.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 126.047 | 100.6725 | 126.047 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 100.6725 | 1086.2955 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 97.8302 | 1083.4532 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 93.209 | 1078.832 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 84.8604 | 1070.4834
[5 empty] | 128 | 977.759 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 133.911 | 108.0485 | 133.911 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 108.0485 | 1085.8075 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 105.1516 | 1082.9106 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 100.4415 | 1078.2005 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 91.9324 | 1069.6914
[5 empty] | 130 | 969.772 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 141.898 | 115.5476 | 141.898 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 115.5476 | 1085.3196 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 112.596 | 1082.368 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 107.797 | 1077.569 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 99.1273 | 1068.8993
[5 empty] | 132 | 981.785 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 129.885 | 103.0466 | 129.885 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 103.0466 | 1084.8316 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 100.0403 | 1081.8253 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 95.1525 | 1076.9375 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 86.3223 | 1068.1073
[5 empty] | 134 | 991.458 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 120.212 | 92.8856 | 120.212 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 92.8856 | 1084.3436 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 89.8247 | 1081.2827 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 84.848 | 1076.306 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 75.8572 | 1067.3152
[5 empty] | 136 | 987.77 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 123.9 | 96.0857 | 123.9 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 96.0857 | 1083.8557 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 92.9701 | 1080.7401 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 87.9045 | 1075.6745 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 78.7532 | 1066.5232
[5 empty] | 138 | 982.725 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 128.945 | 100.6427 | 128.945 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 100.6427 | 1083.3677 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 97.4724 | 1080.1974 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 92.318 | 1075.043 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 83.0061 | 1065.7311
[5 empty] | 140 | 977.559 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 134.111 | 105.3207 | 134.111 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 105.3207 | 1082.8797 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 102.0958 | 1079.6548 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 96.8525 | 1074.4115 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 87.3801 | 1064.9391
[5 empty] | 142 | 975.289 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 136.381 | 107.1027 | 136.381 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 107.1027 | 1082.3917 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 103.8232 | 1079.1122 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 98.491 | 1073.78 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 88.858 | 1064.147
[5 empty] | 144 | 973.968 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 137.702 | 107.9358 | 137.702 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 107.9358 | 1081.9038 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 104.6015 | 1078.5695 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 99.1805 | 1073.1485 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 89.387 | 1063.355
[5 empty] | 146 | 962.473 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 149.197 | 118.9428 | 149.197 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 118.9428 | 1081.4158 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 115.5539 | 1078.0269 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 110.044 | 1072.517 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 100.0899 | 1062.5629
[5 empty] | 148 | 951.285 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 160.385 | 129.6428 | 160.385 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 129.6428 | 1080.9278 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 126.1993 | 1077.4843 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 120.6005 | 1071.8855 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 110.4859 | 1061.7709
[5 empty] | 150 | 948.174 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 163.496 | 132.2659 | 163.496 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 132.2659 | 1080.4399 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 128.7677 | 1076.9417 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 123.08 | 1071.254 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 112.8048 | 1060.9788
[5 empty] | 152 | 944.641 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 167.029 | 135.3109 | 167.029 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 135.3109 | 1079.9519 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 131.758 | 1076.399 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 125.9815 | 1070.6225 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 115.5458 | 1060.1868
[5 empty] | 154 | 941.566 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 170.104 | 137.8979 | 170.104 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 137.8979 | 1079.4639 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 134.2904 | 1075.8564 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 128.425 | 1069.991 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 117.8287 | 1059.3947
[5 empty] | 156 | 940.942 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 170.728 | 138.0339 | 170.728 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 138.0339 | 1078.9759 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 134.3718 | 1075.3138 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 128.4175 | 1069.3595 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 117.6607 | 1058.6027
[5 empty] | 158 | 939.726 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 171.944 | 138.762 | 171.944 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 138.762 | 1078.488 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 135.0451 | 1074.7711 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 129.002 | 1068.728 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 118.0846 | 1057.8106
[5 empty] | 160 | 936.738 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 174.932 | 141.262 | 174.932 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 141.262 | 1078 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 137.4905 | 1074.2285 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 131.3585 | 1068.0965 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 120.2806 | 1057.0186
[5 empty] | 162 | 933.65 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 178.02 | 143.862 | 178.02 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 143.862 | 1077.512 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 140.0359 | 1073.6859 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 133.815 | 1067.465 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 122.5765 | 1056.2265
[5 empty] | 164 | 932.745 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 178.925 | 144.2791 | 178.925 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 144.2791 | 1077.0241 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 140.3982 | 1073.1432 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 134.0885 | 1066.8335 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 122.6895 | 1055.4345
[5 empty] | 166 | 931.696 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 179.974 | 144.8401 | 179.974 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 144.8401 | 1076.5361 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 140.9046 | 1072.6006 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 134.506 | 1066.202 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 122.9464 | 1054.6424
[5 empty] | 168 | 930.999 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 180.671 | 145.0491 | 180.671 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 145.0491 | 1076.0481 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 141.059 | 1072.058 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 134.5715 | 1065.5705 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 122.8514 | 1053.8504
[5 empty] | 170 | 930.885 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 180.785 | 144.6752 | 180.785 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 144.6752 | 1075.5602 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 140.6304 | 1071.5154 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 134.054 | 1064.939 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 122.1733 | 1053.0583
[5 empty] | 172 | 930.378 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 181.292 | 144.6942 | 181.292 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 144.6942 | 1075.0722 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 140.5947 | 1070.9727 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 133.9295 | 1064.3075 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 121.8883 | 1052.2663
[5 empty] | 174 | 931.324 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 180.346 | 143.2602 | 180.346 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 143.2602 | 1074.5842 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 139.1061 | 1070.4301 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 132.352 | 1063.676 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 120.1502 | 1051.4742
[5 empty] | 176 | 933.53 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 178.14 | 140.5662 | 178.14 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 140.5662 | 1074.0962 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 136.3575 | 1069.8875 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 129.5145 | 1063.0445 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 117.1522 | 1050.6822
[5 empty] | 178 | 932.714 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 178.956 | 140.8943 | 178.956 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 140.8943 | 1073.6083 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 136.6308 | 1069.3448 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 129.699 | 1062.413 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 117.1761 | 1049.8901
[5 empty] | 180 | 928.311 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 183.359 | 144.8093 | 183.359 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 144.8093 | 1073.1203 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 140.4912 | 1068.8022 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 133.4705 | 1061.7815 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 120.7871 | 1049.0981
[5 empty] | 182 | 924.179 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 187.491 | 148.4533 | 187.491 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 148.4533 | 1072.6323 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 144.0806 | 1068.2596 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 136.971 | 1061.15 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 124.127 | 1048.306
[5 empty] | 184 | 928.398 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 183.272 | 143.7464 | 183.272 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 143.7464 | 1072.1444 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 139.3189 | 1067.7169 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 132.1205 | 1060.5185 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 119.116 | 1047.514
[5 empty] | 186 | 930.866 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 180.804 | 140.7904 | 180.804 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 140.7904 | 1071.6564 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 136.3083 | 1067.1743 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 129.021 | 1059.887 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 115.8559 | 1046.7219
[5 empty] | 188 | 928.411 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 183.259 | 142.7574 | 183.259 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 142.7574 | 1071.1684 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 138.2207 | 1066.6317 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 130.8445 | 1059.2555 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 117.5189 | 1045.9299
[5 empty] | 190 | 927.849 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 183.821 | 142.8314 | 183.821 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 142.8314 | 1070.6804 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 138.2401 | 1066.0891 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 130.775 | 1058.624 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 117.2889 | 1045.1379
[5 empty] | 192 | 926.71 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 184.96 | 143.4825 | 184.96 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 143.4825 | 1070.1925 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 138.8364 | 1065.5464 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 131.2825 | 1057.9925 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 117.6358 | 1044.3458
[5 empty] | 194 | 926.201 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 185.469 | 143.5035 | 185.469 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 143.5035 | 1069.7045 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 138.8028 | 1065.0038 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 131.16 | 1057.361 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 117.3528 | 1043.5538
[5 empty] | 196 | 924.509 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 187.161 | 144.7075 | 187.161 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 144.7075 | 1069.2165 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 139.9522 | 1064.4612 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 132.2205 | 1056.7295 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 118.2527 | 1042.7617
[5 empty] | 198 | 923.417 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 188.253 | 145.3116 | 188.253 | 13.8052 | 1488612.6665 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 145.3116 | 1068.7286 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 140.5015 | 1063.9185 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 132.681 | 1056.098 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 118.5527 | 1041.9697
[5 empty] | 200 | 923.011 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 188.659 | 145.2296 | 188.659 | 13.835 | 1491802.7991 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 145.2296 | 1068.2406 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 140.3649 | 1063.3759 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 132.4555 | 1055.4665 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 118.1666 | 1041.1776
[5 empty] | 202 | 921.969 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 189.701 | 145.7836 | 189.701 | 13.9114 | 1499989.8822 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 145.7836 | 1067.7526 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 140.8643 | 1062.8333 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 132.866 | 1054.835 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 118.4166 | 1040.3856
[5 empty] | 204 | 920.661 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 191.009 | 146.6036 | 191.009 | 14.0073 | 1510266.1346 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 146.6036 | 1067.2646 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 141.6296 | 1062.2906 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 133.5425 | 1054.2035 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 118.9325 | 1039.5935
[5 empty] | 206 | 920.243 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 191.427 | 146.5337 | 191.427 | 14.038 | 1513549.9444 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 146.5337 | 1066.7767 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 141.505 | 1061.748 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 133.329 | 1053.572 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 118.5585 | 1038.8015
[5 empty] | 208 | 919.297 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 192.373 | 146.9917 | 192.373 | 14.1074 | 1520981.3822 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 146.9917 | 1066.2887 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 141.9084 | 1061.2054 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 133.6435 | 1052.9405 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 118.7124 | 1038.0094
[5 empty] | 210 | 917.533 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 194.137 | 148.2677 | 194.137 | 14.2367 | 1534837.4676 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 148.2677 | 1065.8007 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 143.1297 | 1060.6627 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 134.776 | 1052.309 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 119.6844 | 1037.2174
[5 empty] | 212 | 917.684 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 193.986 | 147.6288 | 193.986 | 14.2256 | 1533651.4388 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 147.6288 | 1065.3128 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 142.4361 | 1060.1201 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 133.9935 | 1051.6775 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 118.7413 | 1036.4253
[5 empty] | 214 | 915.724 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 195.946 | 149.1008 | 195.946 | 14.3694 | 1549045.3101 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 149.1008 | 1064.8248 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 143.8535 | 1059.5775 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 135.322 | 1051.046 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 119.9093 | 1035.6333
[5 empty] | 216 | 915.73 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 195.94 | 148.6068 | 195.94 | 14.3689 | 1548998.1891 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 148.6068 | 1064.3368 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 143.3049 | 1059.0349 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 134.6845 | 1050.4145 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 119.1112 | 1034.8412
[5 empty] | 218 | 915.584 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 196.086 | 148.2649 | 196.086 | 14.3796 | 1550144.7944 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 148.2649 | 1063.8489 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 142.9082 | 1058.4922 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 134.199 | 1049.783 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 118.4652 | 1034.0492
[5 empty] | 220 | 915.444 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 196.226 | 147.9169 | 196.226 | 14.3899 | 1551244.2682 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 147.9169 | 1063.3609 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 142.5056 | 1057.9496 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 133.7075 | 1049.1515 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 117.8131 | 1033.2571
[5 empty] | 222 | 913.52 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 198.15 | 149.3529 | 198.15 | 14.531 | 1566353.1271 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 149.3529 | 1062.8729 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 143.887 | 1057.407 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 135 | 1048.52 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 118.9451 | 1032.4651
[5 empty] | 224 | 912.524 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 199.146 | 149.8609 | 199.146 | 14.604 | 1574173.7816 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 149.8609 | 1062.3849 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 144.3403 | 1056.8643 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 135.3645 | 1047.8885 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 119.149 | 1031.673
[5 empty] | 226 | 912.565 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 199.105 | 149.332 | 199.105 | 14.601 | 1573851.8574 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 149.332 | 1061.897 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 143.7567 | 1056.3217 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 134.692 | 1047.257 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 118.316 | 1030.881
[5 empty] | 228 | 913.484 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 198.186 | 147.925 | 198.186 | 14.5336 | 1566635.8105 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 147.925 | 1061.409 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 142.2951 | 1055.7791 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 133.1415 | 1046.6255 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 116.6049 | 1030.0889
[5 empty] | 230 | 913.545 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 198.125 | 147.376 | 198.125 | 14.5292 | 1566156.8188 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 147.376 | 1060.921 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 141.6914 | 1055.2364 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 132.449 | 1045.994 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 115.7519 | 1029.2969
[5 empty] | 232 | 914.546 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 197.124 | 145.8871 | 197.124 | 14.4558 | 1558296.3605 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 145.8871 | 1060.4331 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 140.1478 | 1054.6938 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 130.8165 | 1045.3625 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 113.9588 | 1028.5048
[5 empty] | 234 | 918.285 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 193.385 | 141.6601 | 193.385 | 14.1816 | 1528930.7669 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 141.6601 | 1059.9451 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 135.8662 | 1054.1512 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 126.446 | 1044.731 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 109.4278 | 1027.7128
[5 empty] | 236 | 919.357 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 192.313 | 140.1001 | 192.313 | 14.103 | 1520510.0578 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 140.1001 | 1059.4571 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 134.2516 | 1053.6086 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 124.7425 | 1044.0995 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 107.5637 | 1026.9207
[5 empty] | 238 | 918.649 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 193.021 | 140.3201 | 193.021 | 14.1549 | 1526071.5646 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 140.3201 | 1058.9691 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 134.4169 | 1053.0659 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 124.819 | 1043.468 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 107.4797 | 1026.1287
[5 empty] | 240 | 922.974 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 188.696 | 135.5072 | 188.696 | 13.8377 | 1492093.5211 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 135.5072 | 1058.4812 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 129.5493 | 1052.5233 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 119.8625 | 1042.8365 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 102.3626 | 1025.3366
[5 empty] | 242 | 927.375 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 184.295 | 130.6182 | 184.295 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 130.6182 | 1057.9932 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 124.6057 | 1051.9807 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 114.83 | 1042.205 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 97.1696 | 1024.5446
[5 empty] | 244 | 929.253 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 182.417 | 128.2522 | 182.417 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 128.2522 | 1057.5052 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 122.185 | 1051.438 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 112.3205 | 1041.5735 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 94.4995 | 1023.7525
[5 empty] | 246 | 930.863 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 180.807 | 126.1543 | 180.807 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 126.1543 | 1057.0173 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 120.0324 | 1050.8954 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 110.079 | 1040.942 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 92.0975 | 1022.9605
[5 empty] | 248 | 931.924 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 179.746 | 124.6053 | 179.746 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 124.6053 | 1056.5293 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 118.4288 | 1050.3528 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 108.3865 | 1040.3105 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 90.2444 | 1022.1684
[5 empty] | 250 | 936.722 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 174.948 | 119.3193 | 174.948 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 119.3193 | 1056.0413 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 113.0881 | 1049.8101 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 102.957 | 1039.679 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 84.6544 | 1021.3764
[5 empty] | 252 | 941.777 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 169.893 | 113.7763 | 169.893 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 113.7763 | 1055.5533 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 107.4905 | 1049.2675 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 97.2705 | 1039.0475 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 78.8073 | 1020.5843
[5 empty] | 254 | 948.143 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 163.527 | 106.9224 | 163.527 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 106.9224 | 1055.0654 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 100.5819 | 1048.7249 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 90.273 | 1038.416 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 71.6493 | 1019.7923
[5 empty] | 256 | 955.417 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 156.253 | 99.1604 | 156.253 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 99.1604 | 1054.5774 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 92.7653 | 1048.1823 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 82.3675 | 1037.7845 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 63.5832 | 1019.0002
[5 empty] | 258 | 962.7 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 148.97 | 91.3894 | 148.97 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 91.3894 | 1054.0894 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 84.9396 | 1047.6396 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 74.453 | 1037.153 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 55.5082 | 1018.2082
[5 empty] | 260 | 969.281 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 142.389 | 84.3205 | 142.389 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 84.3205 | 1053.6015 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 77.816 | 1047.097 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 67.2405 | 1036.5215 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 48.1351 | 1017.4161
[5 empty] | 262 | 980.284 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 131.386 | 72.8295 | 131.386 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 72.8295 | 1053.1135 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 66.2704 | 1046.5544 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 55.606 | 1035.89 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 36.3401 | 1016.6241
[5 empty] | 264 | 986.551 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 125.119 | 66.0745 | 125.119 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 66.0745 | 1052.6255 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 59.4607 | 1046.0117 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 48.7075 | 1035.2585 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 29.281 | 1015.832
[5 empty] | 266 | 989.198 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 122.472 | 62.9396 | 122.472 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 62.9396 | 1052.1376 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 56.2711 | 1045.4691 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 45.429 | 1034.627 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 25.842 | 1015.04
[5 empty] | 268 | 994.39 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 117.28 | 57.2596 | 117.28 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 57.2596 | 1051.6496 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 50.5365 | 1044.9265 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 39.6055 | 1033.9955 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 19.8579 | 1014.2479
[5 empty] | 270 | 999.917 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 111.753 | 51.2446 | 111.753 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 51.2446 | 1051.1616 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 44.4668 | 1044.3838 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 33.447 | 1033.364 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 13.5389 | 1013.4559
[5 empty] | 272 | 1004.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 107.047 | 46.0506 | 107.047 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 46.0506 | 1050.6736 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 39.2182 | 1043.8412 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 28.1095 | 1032.7325 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 8.0408 | 1012.6638
|  |  |  | Reservoir | 274 | 1008.819 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 10 | 170 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 160 | 10 | 1178.819 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 160 | 170 | 1178.819 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 160 | 170 | 1178.819 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 160 | 170 | 1178.819
[5 empty] | 276 | 1007.834 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 170.497 | 170.4424 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 170.497 | 1178.331 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 170.4424 | 1178.2764 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 170.3535 | 1178.1875 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 170.193 | 1178.027
[5 empty] | 278 | 1005.626 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 172.2171 | 172.1077 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 172.2171 | 1177.8431 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 172.1077 | 1177.7337 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 171.93 | 1177.556 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 171.6089 | 1177.2349
[5 empty] | 280 | 1001.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 175.7321 | 175.5681 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 175.7321 | 1177.3551 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 175.5681 | 1177.1911 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 175.3015 | 1176.9245 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 174.8199 | 1176.4429
[5 empty] | 282 | 1004.052 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 172.8151 | 172.5965 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 172.8151 | 1176.8671 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 172.5965 | 1176.6485 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 172.241 | 1176.293 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 171.5988 | 1175.6508
[5 empty] | 284 | 1010.797 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 165.5821 | 165.3088 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 165.5821 | 1176.3791 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 165.3088 | 1176.1058 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 164.8645 | 1175.6615 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 164.0618 | 1174.8588
[5 empty] | 286 | 1014.67 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 161.2212 | 160.8932 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 161.2212 | 1175.8912 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 160.8932 | 1175.5632 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 160.36 | 1175.03 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 159.3967 | 1174.0667
[5 empty] | 288 | 1017.319 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 158.0842 | 157.7016 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 158.0842 | 1175.4032 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 157.7016 | 1175.0206 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 157.0795 | 1174.3985 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 155.9557 | 1173.2747
[5 empty] | 290 | 1027.459 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 147.4562 | 147.019 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 147.4562 | 1174.9152 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 147.019 | 1174.478 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 146.308 | 1173.767 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 145.0236 | 1172.4826
[5 empty] | 292 | 1031.99 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 142.4373 | 141.9453 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 142.4373 | 1174.4273 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 141.9453 | 1173.9353 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 141.1455 | 1173.1355 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 139.7006 | 1171.6906
[5 empty] | 294 | 1036.254 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 137.6853 | 137.1387 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 137.6853 | 1173.9393 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 137.1387 | 1173.3927 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 136.25 | 1172.504 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 134.6445 | 1170.8985
[5 empty] | 296 | 1040.127 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 133.3243 | 132.7231 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 133.3243 | 1173.4513 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 132.7231 | 1172.8501 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 131.7455 | 1171.8725 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 129.9795 | 1170.1065
[5 empty] | 298 | 1044.396 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 128.5673 | 127.9114 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 128.5673 | 1172.9633 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 127.9114 | 1172.3074 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 126.845 | 1171.241 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 124.9184 | 1169.3144
[5 empty] | 300 | 1051.339 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 121.1364 | 120.4258 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 121.1364 | 1172.4754 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 120.4258 | 1171.7648 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 119.2705 | 1170.6095 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 117.1834 | 1168.5224
[5 empty] | 302 | 1060.955 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 111.0324 | 110.2672 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 111.0324 | 1171.9874 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 110.2672 | 1171.2222 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 109.023 | 1169.978 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 106.7753 | 1167.7303
[5 empty] | 304 | 1070.227 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 101.2724 | 100.4525 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 101.2724 | 1171.4994 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 100.4525 | 1170.6795 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 99.1195 | 1169.3465 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 96.7113 | 1166.9383
[5 empty] | 306 | 1072.691 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 98.3205 | 97.4459 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 98.3205 | 1171.0115 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 97.4459 | 1170.1369 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 96.024 | 1168.715 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 93.4552 | 1166.1462
[5 empty] | 308 | 1076.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 94.0205 | 93.0913 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 94.0205 | 1170.5235 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 93.0913 | 1169.5943 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 91.5805 | 1168.0835 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 88.8512 | 1165.3542
[5 empty] | 310 | 1083.996 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 86.0395 | 85.0557 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 86.0395 | 1170.0355 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 85.0557 | 1169.0517 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 83.456 | 1167.452 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 80.5661 | 1164.5621
[5 empty] | 312 | 1097.188 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 72.3596 | 71.321 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 72.3596 | 1169.5476 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 71.321 | 1168.509 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 69.6325 | 1166.8205 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 66.5821 | 1163.7701
[5 empty] | 314 | 1103.545 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 65.5146 | 64.4214 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 65.5146 | 1169.0596 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 64.4214 | 1167.9664 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 62.644 | 1166.189 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 59.433 | 1162.978
[5 empty] | 316 | 1105.174 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 63.3976 | 62.2498 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 63.3976 | 1168.5716 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 62.2498 | 1167.4238 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 60.3835 | 1165.5575 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 57.012 | 1162.186
[5 empty] | 318 | 1111.657 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 56.4266 | 55.2241 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 56.4266 | 1168.0836 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 55.2241 | 1166.8811 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 53.269 | 1164.926 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 49.7369 | 1161.3939
[5 empty] | 320 | 1122.935 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 44.6607 | 43.4035 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 44.6607 | 1167.5957 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 43.4035 | 1166.3385 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 41.3595 | 1164.2945 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 37.6669 | 1160.6019
[5 empty] | 322 | 1128.197 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 38.9107 | 37.5989 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 38.9107 | 1167.1077 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 37.5989 | 1165.7959 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 35.466 | 1163.663 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 31.6128 | 1159.8098
[5 empty] | 324 | 1132.561 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 34.0587 | 32.6922 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 34.0587 | 1166.6197 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 32.6922 | 1165.2532 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 30.4705 | 1163.0315 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 26.4568 | 1159.0178
[5 empty] | 326 | 1131.854 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 34.2778 | 32.8566 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 34.2778 | 1166.1318 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 32.8566 | 1164.7106 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 30.546 | 1162.4 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 26.3717 | 1158.2257
[5 empty] | 328 | 1133.338 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 32.3058 | 30.83 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 32.3058 | 1165.6438 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 30.83 | 1164.168 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 28.4305 | 1161.7685 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 24.0957 | 1157.4337
[5 empty] | 330 | 1136.405 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 28.7508 | 27.2204 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 28.7508 | 1165.1558 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 27.2204 | 1163.6254 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 24.732 | 1161.137 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 20.2366 | 1156.6416
[5 empty] | 332 | 1128.709 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 35.9588 | 34.3737 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 35.9588 | 1164.6678 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 34.3737 | 1163.0827 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 31.7965 | 1160.5055 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 27.1406 | 1155.8496
[5 empty] | 334 | 1120.713 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 43.4669 | 41.8271 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 43.4669 | 1164.1799 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 41.8271 | 1162.5401 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 39.161 | 1159.874 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 34.3445 | 1155.0575
[5 empty] | 336 | 1115.226 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 47.5999 | 45.8034 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 47.5999 | 1162.8259 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 45.8034 | 1161.0294 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 42.8816 | 1158.1076 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 37.5985 | 1152.8245
[5 empty] | 338 | 1108.709 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 52.7629 | 50.8097 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 52.7629 | 1161.4719 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 50.8097 | 1159.5187 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 47.6321 | 1156.3411 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 41.8824 | 1150.5914
[5 empty] | 340 | 1102.499 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 57.6189 | 55.509 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 57.6189 | 1160.1179 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 55.509 | 1158.008 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 52.0757 | 1154.5747 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 45.8594 | 1148.3584
[5 empty] | 342 | 1096.349 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 62.4149 | 60.1483 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 62.4149 | 1158.7639 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 60.1483 | 1156.4973 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 56.4593 | 1152.8083 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 49.7763 | 1146.1253
[5 empty] | 344 | 1090.39 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 67.02 | 64.5966 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 67.02 | 1157.41 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 64.5966 | 1154.9866 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 60.6519 | 1151.0419 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 53.5023 | 1143.8923
[5 empty] | 346 | 1087.765 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 68.291 | 65.7109 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 68.291 | 1156.056 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 65.7109 | 1153.4759 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 61.5104 | 1149.2754 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 53.8942 | 1141.6592
[5 empty] | 348 | 1084.661 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 70.041 | 67.3042 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 70.041 | 1154.702 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 67.3042 | 1151.9652 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 62.848 | 1147.509 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 54.7652 | 1139.4262
[5 empty] | 350 | 1081.662 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 71.686 | 68.7925 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 71.686 | 1153.348 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 68.7925 | 1150.4545 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 64.0806 | 1145.7426 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.5312 | 1137.1932
[5 empty] | 352 | 1076.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 75.122 | 72.0718 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 75.122 | 1151.994 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 72.0718 | 1148.9438 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 67.1042 | 1143.9762 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 58.0881 | 1134.9601
[5 empty] | 354 | 1070.898 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 79.7421 | 76.5351 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 79.7421 | 1150.6401 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 76.5351 | 1147.4331 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 71.3117 | 1142.2097 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 61.8291 | 1132.7271
[5 empty] | 356 | 1065.018 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 84.2681 | 80.9044 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 84.2681 | 1149.2861 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 80.9044 | 1145.9224 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 75.4253 | 1140.4433 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 65.476 | 1130.494
[5 empty] | 358 | 1059.58 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 88.3521 | 84.8317 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 88.3521 | 1147.9321 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 84.8317 | 1144.4117 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 79.0969 | 1138.6769 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 68.681 | 1128.261
[5 empty] | 360 | 1055.284 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 91.2941 | 87.617 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 91.2941 | 1146.5781 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 87.617 | 1142.901 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 81.6265 | 1136.9105 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 70.7439 | 1126.0279
[5 empty] | 362 | 1050.886 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 94.3381 | 90.5043 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 94.3381 | 1145.2241 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 90.5043 | 1141.3903 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 84.258 | 1135.144 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 72.9089 | 1123.7949
[5 empty] | 364 | 1052.647 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 91.2231 | 87.2326 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 91.2231 | 1143.8701 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 87.2326 | 1139.8796 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 80.7306 | 1133.3776 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 68.9148 | 1121.5618
[5 empty] | 366 | 1051.117 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 91.3992 | 87.2519 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 91.3992 | 1142.5162 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 87.2519 | 1138.3689 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 80.4942 | 1131.6112 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 68.2118 | 1119.3288
[5 empty] | 368 | 1048.266 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 92.8962 | 88.5922 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.8962 | 1141.1622 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 88.5922 | 1136.8582 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 81.5788 | 1129.8448 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 68.8298 | 1117.0958
[5 empty] | 370 | 1040.172 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 99.6362 | 95.1755 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 99.6362 | 1139.8082 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 95.1755 | 1135.3475 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 87.9063 | 1128.0783 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 74.6907 | 1114.8627
[5 empty] | 372 | 1033.483 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 104.9712 | 100.3538 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 104.9712 | 1138.4542 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 100.3538 | 1133.8368 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 92.8289 | 1126.3119 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 79.1467 | 1112.6297
[5 empty] | 374 | 1030.95 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 106.1502 | 101.3761 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 106.1502 | 1137.1002 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 101.3761 | 1132.3261 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 93.5955 | 1124.5455 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 79.4466 | 1110.3966
[5 empty] | 376 | 1032.263 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 103.4833 | 98.5524 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 103.4833 | 1135.7463 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 98.5524 | 1130.8154 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 90.5161 | 1122.7791 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 75.9006 | 1108.1636
[5 empty] | 378 | 1031.391 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 103.0013 | 97.9137 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 103.0013 | 1134.3923 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 97.9137 | 1129.3047 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 89.6216 | 1121.0126 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 74.5395 | 1105.9305
[5 empty] | 380 | 1025.791 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 107.2473 | 102.003 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 107.2473 | 1133.0383 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 102.003 | 1127.794 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 93.4552 | 1119.2462 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 77.9065 | 1103.6975
[5 empty] | 382 | 1020.911 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 110.7733 | 105.3724 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 110.7733 | 1131.6843 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 105.3724 | 1126.2834 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 96.5688 | 1117.4798 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 80.5534 | 1101.4644
[5 empty] | 384 | 1015.65 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 114.6803 | 109.1227 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 114.6803 | 1130.3303 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 109.1227 | 1124.7727 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 100.0634 | 1115.7134 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 83.5814 | 1099.2314
[5 empty] | 386 | 1012.139 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 116.8373 | 111.123 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 116.8373 | 1128.9763 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 111.123 | 1123.262 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 101.8079 | 1113.9469 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 84.8594 | 1096.9984
[5 empty] | 388 | 1010.472 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 117.1504 | 111.2793 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 117.1504 | 1127.6224 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 111.2793 | 1121.7513 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 101.7085 | 1112.1805 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 84.2933 | 1094.7653
[5 empty] | 390 | 1005.401 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 120.8674 | 114.8396 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 120.8674 | 1126.2684 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 114.8396 | 1120.2406 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 105.0131 | 1110.4141 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 87.1313 | 1092.5323
[5 empty] | 392 | 996.666 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 128.2484 | 122.0639 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 128.2484 | 1124.9144 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 122.0639 | 1118.7299 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 111.9817 | 1108.6477 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 93.6332 | 1090.2992
[5 empty] | 394 | 991.35 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 132.2104 | 125.8692 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 132.2104 | 1123.5604 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 125.8692 | 1117.2192 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 115.5312 | 1106.8812 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 96.7162 | 1088.0662
[5 empty] | 396 | 990.486 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 131.7204 | 125.2225 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 131.7204 | 1122.2064 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 125.2225 | 1115.7085 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 114.6288 | 1105.1148 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 95.3471 | 1085.8331
[5 empty] | 398 | 992.761 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 128.0915 | 121.4368 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 128.0915 | 1120.8525 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 121.4368 | 1114.1978 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 110.5874 | 1103.3484 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 90.8391 | 1083.6001
[5 empty] | 400 | 999.077 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 120.4215 | 113.6101 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 120.4215 | 1119.4985 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 113.6101 | 1112.6871 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 102.505 | 1101.582 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 82.29 | 1081.367
[5 empty] | 402 | 1001.8 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 116.3445 | 109.3764 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 116.3445 | 1118.1445 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 109.3764 | 1111.1764 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 98.0155 | 1099.8155 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 77.334 | 1079.134
[5 empty] | 404 | 1002.224 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 114.5665 | 107.4417 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 114.5665 | 1116.7905 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 107.4417 | 1109.6657 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 95.8251 | 1098.0491 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 74.677 | 1076.901
[5 empty] | 406 | 1002.003 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 113.4335 | 106.152 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 113.4335 | 1115.4365 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 106.152 | 1108.155 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 94.2797 | 1096.2827 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 72.6649 | 1074.6679
[5 empty] | 408 | 1003.596 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 110.4865 | 103.0483 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 110.4865 | 1114.0825 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 103.0483 | 1106.6443 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 90.9203 | 1094.5163 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 68.8389 | 1072.4349
[5 empty] | 410 | 994.111 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 118.6176 | 111.0226 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 118.6176 | 1112.7286 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 111.0226 | 1105.1336 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 98.6388 | 1092.7498 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 76.0908 | 1070.2018
[5 empty] | 412 | 983.925 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 127.4496 | 119.6979 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 127.4496 | 1111.3746 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 119.6979 | 1103.6229 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 107.0584 | 1090.9834 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 84.0438 | 1067.9688
[5 empty] | 414 | 972.347 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 137.6736 | 129.7652 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 137.6736 | 1110.0206 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 129.7652 | 1102.1122 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 116.87 | 1089.217 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 93.3887 | 1065.7357
[5 empty] | 416 | 963.901 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 144.7656 | 136.7005 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 144.7656 | 1108.6666 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 136.7005 | 1100.6015 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 123.5496 | 1087.4506 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 99.6017 | 1063.5027
[5 empty] | 418 | 963.258 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 144.0546 | 135.8328 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 144.0546 | 1107.3126 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 135.8328 | 1099.0908 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 122.4261 | 1085.6841 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 98.0116 | 1061.2696
[5 empty] | 420 | 965.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 140.0866 | 131.7081 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 140.0866 | 1105.9586 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 131.7081 | 1097.5801 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 118.0457 | 1083.9177 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 93.1646 | 1059.0366
[5 empty] | 422 | 966.177 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 138.4277 | 129.8924 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 138.4277 | 1104.6047 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 129.8924 | 1096.0694 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 115.9743 | 1082.1513 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 90.6266 | 1056.8036
[5 empty] | 424 | 973.825 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 129.4257 | 120.7337 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 129.4257 | 1103.2507 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 120.7337 | 1094.5587 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 106.5599 | 1080.3849 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 80.7455 | 1054.5705
[5 empty] | 426 | 983.972 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 117.9247 | 109.076 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 117.9247 | 1101.8967 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 109.076 | 1093.048 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 94.6464 | 1078.6184 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 68.3655 | 1052.3375
[5 empty] | 428 | 994.096 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 106.4467 | 97.4413 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 106.4467 | 1100.5427 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 97.4413 | 1091.5373 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 82.756 | 1076.852 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 56.0084 | 1050.1044
[5 empty] | 430 | 991.695 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 107.4937 | 98.3316 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 107.4937 | 1099.1887 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 98.3316 | 1090.0266 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 83.3906 | 1075.0856 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 56.1764 | 1047.8714
[5 empty] | 432 | 984.933 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 112.9018 | 103.5829 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 112.9018 | 1097.8348 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 103.5829 | 1088.5159 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 88.3862 | 1073.3192 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 60.7053 | 1045.6383
[5 empty] | 434 | 974.509 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 121.9718 | 112.4962 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 121.9718 | 1096.4808 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 112.4962 | 1087.0052 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 97.0437 | 1071.5527 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 68.8963 | 1043.4053
[5 empty] | 436 | 966.698 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 128.4288 | 118.7965 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 128.4288 | 1095.1268 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 118.7965 | 1085.4945 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 103.0883 | 1069.7863 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 74.4742 | 1041.1722
[5 empty] | 438 | 963.618 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 130.1548 | 120.3658 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 130.1548 | 1093.7728 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 120.3658 | 1083.9838 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 104.4019 | 1068.0199 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 75.3212 | 1038.9392
[5 empty] | 440 | 957.803 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 134.6158 | 124.6701 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 134.6158 | 1092.4188 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 124.6701 | 1082.4731 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 108.4505 | 1066.2535 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 78.9031 | 1036.7061
[5 empty] | 442 | 954.277 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 136.7878 | 126.6854 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 136.7878 | 1091.0648 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 126.6854 | 1080.9624 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 110.21 | 1064.487 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 80.1961 | 1034.4731
[5 empty] | 444 | 947.182 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 142.5289 | 132.2697 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 142.5289 | 1089.7109 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 132.2697 | 1079.4517 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 115.5386 | 1062.7206 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 85.0581 | 1032.2401
[5 empty] | 446 | 938.045 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 150.3119 | 139.896 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 150.3119 | 1088.3569 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 139.896 | 1077.941 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 122.9092 | 1060.9542 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 91.962 | 1030.007
[5 empty] | 448 | 930.871 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 156.1319 | 145.5593 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 156.1319 | 1087.0029 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 145.5593 | 1076.4303 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 128.3168 | 1059.1878 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 96.903 | 1027.774
[5 empty] | 450 | 926.391 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 159.2579 | 148.5286 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 159.2579 | 1085.6489 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 148.5286 | 1074.9196 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 131.0303 | 1057.4213 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 99.1499 | 1025.5409
[5 empty] | 452 | 918.344 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 165.9509 | 155.0649 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 165.9509 | 1084.2949 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 155.0649 | 1073.4089 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 137.3109 | 1055.6549 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 104.9639 | 1023.3079
[5 empty] | 454 | 911.505 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 171.436 | 160.3932 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 171.436 | 1082.941 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 160.3932 | 1071.8982 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 142.3835 | 1053.8885 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 109.5698 | 1021.0748
[5 empty] | 456 | 903.61 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 177.977 | 166.7775 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 177.977 | 1081.587 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 166.7775 | 1070.3875 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 148.5121 | 1052.1221 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 115.2318 | 1018.8418
[5 empty] | 458 | 900.63 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 179.603 | 168.2468 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 179.603 | 1080.233 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 168.2468 | 1068.8768 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 149.7256 | 1050.3556 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 115.9787 | 1016.6087
[5 empty] | 460 | 904.066 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 174.813 | 163.3001 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 174.813 | 1078.879 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 163.3001 | 1067.3661 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 144.5232 | 1048.5892 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 110.3097 | 1014.3757
[5 empty] | 462 | 915.092 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 162.433 | 150.7635 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 162.433 | 1077.525 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 150.7635 | 1065.8555 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 131.7308 | 1046.8228 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 97.0507 | 1012.1427
[5 empty] | 464 | 905.556 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 170.615 | 158.7888 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 170.615 | 1076.171 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 158.7888 | 1064.3448 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 139.5004 | 1045.0564 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 104.3536 | 1009.9096
[5 empty] | 466 | 905.271 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 169.5461 | 157.5631 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 169.5461 | 1074.8171 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 157.5631 | 1062.8341 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 138.0189 | 1043.2899 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 102.4056 | 1007.6766
[5 empty] | 468 | 901.918 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 171.5451 | 159.4054 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 171.5451 | 1073.4631 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 159.4054 | 1061.3234 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 139.6055 | 1041.5235 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 103.5255 | 1005.4435
[5 empty] | 470 | 895.651 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 176.4581 | 164.1617 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 176.4581 | 1072.1091 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 164.1617 | 1059.8127 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 144.1061 | 1039.7571 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 107.5595 | 1003.2105
[5 empty] | 472 | 892.304 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 178.4511 | 165.998 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 178.4511 | 1070.7551 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 165.998 | 1058.302 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 145.6867 | 1037.9907 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 108.6734 | 1000.9774
[5 empty] | 474 | 895.279 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 174.1221 | 161.5123 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 174.1221 | 1069.4011 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 161.5123 | 1056.7913 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 140.9452 | 1036.2242 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 103.4654 | 998.7444
[5 empty] | 476 | 896.818 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 171.2292 | 158.4626 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 171.2292 | 1068.0472 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 158.4626 | 1055.2806 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 137.6398 | 1034.4578 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 99.6933 | 996.5113
[5 empty] | 478 | 909.921 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 154.6935 | 141.5186 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 154.6935 | 1064.6145 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 141.5186 | 1051.4396 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 120.0272 | 1029.9482 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 80.8484 | 990.7694
[5 empty] | 480 | 926.295 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 134.8869 | 121.3036 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 134.8869 | 1061.1819 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 121.3036 | 1047.5986 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 99.1436 | 1025.4386 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 58.7325 | 985.0275
[5 empty] | 482 | 924.888 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 132.8613 | 118.8696 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 132.8613 | 1057.7493 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 118.8696 | 1043.7576 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 96.041 | 1020.929 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 54.3975 | 979.2855
[5 empty] | 484 | 919.044 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 135.2727 | 120.8727 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 135.2727 | 1054.3167 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 120.8727 | 1039.9167 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 97.3753 | 1016.4193 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 54.4996 | 973.5436
[5 empty] | 486 | 911.164 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 139.7201 | 124.9117 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 139.7201 | 1050.8841 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 124.9117 | 1036.0757 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 100.7457 | 1011.9097 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 56.6377 | 967.8017
[5 empty] | 488 | 903.893 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 143.5585 | 128.3417 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 143.5585 | 1047.4515 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 128.3417 | 1032.2347 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 103.5071 | 1007.4001 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 58.1667 | 962.0597
[5 empty] | 490 | 901.953 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 142.0659 | 126.4407 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 142.0659 | 1044.0189 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 126.4407 | 1028.3937 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 100.9375 | 1002.8905 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 54.3648 | 956.3178
[5 empty] | 492 | 900.198 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 140.3883 | 124.3548 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 140.3883 | 1040.5863 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 124.3548 | 1024.5528 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 98.1828 | 998.3808 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 50.3779 | 950.5759
[5 empty] | 494 | 904.177 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 132.9767 | 116.5348 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 132.9767 | 1037.1537 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 116.5348 | 1020.7118 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 89.6942 | 993.8712 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 40.6569 | 944.8339
[5 empty] | 496 | 912.253 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 121.468 | 104.6178 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 121.468 | 1033.721 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 104.6178 | 1016.8708 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 77.1086 | 989.3616 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 26.839 | 939.092
[5 empty] | 498 | 915.297 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 114.9914 | 97.7328 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 114.9914 | 1030.2884 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 97.7328 | 1013.0298 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 69.555 | 984.852 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 18.053 | 933.35
|  |  |  | Reservoir | 500 | 919.629 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 10 | 10 | 10 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 10 | 929.629 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 10 | 929.629 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 10 | 929.629 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 10 | 929.629
[15 empty] | Total Steel Mass (kg): | 322625353.6026