## Summary
Option 7 Summary
Item | Chainage | Value
Pipeline | 0-8 | 1.9 | m - Diameter
Pump Station | 8 | 50 | m - Pumping Head
Pipeline | 8-22 | 1.9 | m - Diameter
Break Pressure | 22 | 10 | m -Elevation
Pipeline | 22-158 | 1.9 | m - Diameter
Pipeline | 158-228 | 1.8 | m - Diameter
Break Pressure | 228 | 10 | m - Elevation
Pump Station | 228 | 260 | m - Pumping Head
Pipeline | 228-336 | 2.2 | m -Diameter
Pipeline | 336-508 | 1.8 | m -Diameter
Pipeline | 508-520 | 1.5 | m -Diameter

## Control Points
Longitudinal profile data - Botswana pipeline
| OPTION 1: Pipeline goes through Serule before joining to BPT1 | OPTION2: Pipeline goes directly to BPT1
CHAINAGE (km0 | NGL (m) | NGL (m) |  | Botswana 1
2 | 1069.018 | 1069.018 | Start | Botswana 2
4 | 1067.321 | 1067.321
6 | 1064.035 | 1064.035
8 | 1063.832 | 1063.832
10 | 1067.893 | 1067.893
12 | 1075.133 | 1075.133
14 | 1082.768 | 1082.768
16 | 1089.726 | 1089.726
18 | 1094.131 | 1094.131
20 | 1097.897 | 1097.897
22 | 1101.67 | 1101.67
24 | 1095.952 | 1095.952
26 | 1090.107 | 1090.107
28 | 1085.781 | 1085.781
30 | 1081.89 | 1081.89
32 | 1077.937 | 1077.937
34 | 1074.89 | 1074.89
36 | 1071.114 | 1071.114
38 | 1065.311 | 1065.311
40 | 1059.051 | 1059.051
42 | 1054.28 | 1054.28
44 | 1053.871 | 1053.871
46 | 1050.42 | 1050.42
48 | 1052.704 | 1052.704
50 | 1056.355 | 1056.355
52 | 1058.466 | 1058.466
54 | 1055.99 | 1055.99
56 | 1055.66 | 1055.66
58 | 1056.404 | 1056.404
60 | 1056.841 | 1056.841
62 | 1056.377 | 1056.377
64 | 1052.503 | 1052.503
66 | 1046.022 | 1046.022
68 | 1036.575 | 1036.575
70 | 1031.818 | 1031.818
72 | 1027.675 | 1027.675
74 | 1023.844 | 1023.844
76 | 1020.888 | 1020.888
78 | 1023.648 | 1023.648
80 | 1027.566 | 1027.566
82 | 1032.371 | 1032.371
84 | 1034.983 | 1034.983
86 | 1033.213 | 1033.213
88 | 1031.188 | 1031.188
90 | 1029.08 | 1029.08
92 | 1026.322 | 1026.322
94 | 1023.207 | 1023.207
96 | 1021.503 | 1021.503
98 | 1019.765 | 1019.765
100 | 1018.493 | 1018.493
102 | 1016.444 | 1016.444
104 | 1013.288 | 1013.288
106 | 1007.843 | 1007.843
108 | 1001.282 | 1001.282
110 | 996.609 | 996.609
112 | 992.999 | 992.999
114 | 993.639 | 993.639
116 | 994.611 | 994.611
118 | 995.751 | 995.751
120 | 996.479 | 996.479
122 | 996.147 | 996.147
124 | 992.094 | 992.094
126 | 985.623 | 985.623
128 | 977.759 | 977.759
130 | 969.772 | 969.772
132 | 981.785 | 981.785
134 | 991.458 | 991.458
136 | 987.77 | 987.77
138 | 982.725 | 982.725
140 | 977.559 | 977.559
142 | 975.289 | 975.289
144 | 973.968 | 973.968
146 | 962.473 | 962.473
148 | 951.285 | 951.285
150 | 948.174 | 948.174
152 | 944.641 | 944.641
154 | 941.566 | 941.566
156 | 940.942 | 940.942
158 | 939.726 | 939.726
160 | 936.738 | 936.738
162 | 933.65 | 933.65
164 | 932.745 | 932.745
166 | 931.696 | 931.696
168 | 930.999 | 930.999
170 | 930.885 | 930.885
172 | 930.378 | 930.378
174 | 931.324 | 931.324
176 | 933.53 | 933.53
178 | 932.714 | 932.714
180 | 928.311 | 928.311
182 | 924.179 | 924.179
184 | 928.398 | 928.398
186 | 930.866 | 930.866
188 | 928.411 | 928.411
190 | 927.849 | 927.849
192 | 926.71 | 926.71
194 | 926.201 | 926.201
196 | 924.509 | 924.509
198 | 923.417 | 923.417
200 | 923.011 | 923.011
202 | 921.969 | 921.969
204 | 920.661 | 920.661
206 | 920.243 | 920.243
208 | 919.297 | 919.297
210 | 917.533 | 917.533
212 | 917.684 | 917.684
214 | 915.724 | 915.724
216 | 915.73 | 915.73
218 | 915.584 | 915.584
220 | 915.444 | 915.444
222 | 913.52 | 913.52
224 | 912.524 | 912.524
226 | 912.565 | 912.565
228 | 913.484 | 913.484
230 | 913.545 | 913.545
232 | 914.546 | 914.546
234 | 918.285 | 918.285
236 | 919.357 | 919.357
238 | 918.649 | 918.649
240 | 922.974 | 922.974
242 | 927.375 | 927.375
244 | 929.253 | 929.253
246 | 930.863 | 930.863
248 | 931.924 | 931.924
250 | 936.722 | 936.722
252 | 941.777 | 941.777
254 | 948.143 | 948.143
256 | 955.417 | 955.417
258 | 962.7 | 962.7
260 | 969.281 | 969.281
262 | 980.284 | 980.284
264 | 986.551 | 986.551
266 | 989.198 | 989.198
268 | 994.39 | 994.39
270 | 999.917 | 999.917
272 | 1004.623 | 1004.623
274 | 1008.819 | 1008.819
276 | 1007.834 | 1007.834
278 | 1005.626 | 1005.626
280 | 1001.623 | 1001.623
282 | 1004.052 | 1004.052
284 | 1010.797 | 1010.797
286 | 1014.67 | 1014.67
288 | 1017.319 | 1017.319
290 | 1027.459 | 1027.459
292 | 1031.99 | 1031.99
294 | 1036.254 | 1036.254
296 | 1040.127 | 1040.127
298 | 1044.396 | 1044.396
300 | 1051.339 | 1051.339
302 | 1060.955 | 1060.955
304 | 1070.227 | 1070.227
306 | 1072.691 | 1072.691
308 | 1076.503 | 1076.503
310 | 1083.996 | 1083.996
312 | 1097.188 | 1097.188
314 | 1103.545 | 1103.545
316 | 1105.174 | 1105.174
318 | 1111.657 | 1111.657
320 | 1122.935 | 1122.935
322 | 1128.197 | 1128.197
324 | 1132.561 | 1132.561
326 | 1131.854 | 1131.854
328 | 1133.338 | 1133.338
330 | 1136.405 | 1136.405
332 | 1128.709 | 1128.709
334 | 1120.713 | 1120.713
336 | 1115.226 | 1115.226
338 | 1108.709 | 1108.709
340 | 1102.499 | 1102.499
342 | 1096.349 | 1096.349
344 | 1090.39 | 1090.39
346 | 1087.765 | 1087.765
348 | 1084.661 | 1084.661
350 | 1081.662 | 1081.662
352 | 1076.872 | 1076.872
354 | 1070.898 | 1070.898
356 | 1065.018 | 1065.018
358 | 1059.58 | 1059.58
360 | 1055.284 | 1055.284
362 | 1050.886 | 1050.886
364 | 1052.647 | 1052.647
366 | 1051.117 | 1051.117
368 | 1048.266 | 1048.266
370 | 1040.172 | 1040.172
372 | 1033.483 | 1033.483
374 | 1030.95 | 1030.95
376 | 1032.263 | 1032.263
378 | 1031.391 | 1031.391
380 | 1025.791 | 1025.791
382 | 1020.911 | 1020.911
384 | 1015.65 | 1015.65
386 | 1012.139 | 1012.139
388 | 1010.472 | 1010.472
390 | 1005.401 | 1005.401
392 | 996.666 | 996.666
394 | 991.35 | 991.35
396 | 990.486 | 990.486
398 | 992.761 | 992.761
400 | 999.077 | 999.077
402 | 1001.8 | 1001.8
404 | 1002.224 | 1002.224
406 | 1002.003 | 1002.003
408 | 1003.596 | 1003.596
410 | 994.111 | 994.111
412 | 983.925 | 983.925
414 | 972.347 | 972.347
416 | 963.901 | 963.901
418 | 963.258 | 963.258
420 | 965.836 | 965.872
422 | 966.309 | 966.177
424 | 972.884 | 973.825
426 | 983.972 | 983.972
428 | 994.096 | 994.096
430 | 991.695 | 991.695
432 | 984.933 | 984.933
434 | 978.185 | 974.509
436 | 972.686 | 966.698
438 | 966.824 | 963.618
440 | 960.902 | 957.803
442 | 952.924 | 954.277
444 | 945.683 | 947.182
446 | 941.042 | 938.045
448 | 937.104 | 930.871
450 | 939.943 | 926.391
452 | 944.776 | 918.344
454 | 947.762 | 911.505
456 | 952.649 | 903.61
458 | 954.554 | 900.63
460 | 952.37 | 904.066
462 | 947.552 | 915.092
464 | 941.898 | 905.556
466 | 940.521 | 905.271
468 | 939.702 | 901.918
470 | 937.147 | 895.651
472 | 933.872 | 892.304
474 | 933.184 | 895.279
476 | 939.292 | 896.818
478 | 944.619 | 909.921
480 | 954.023 | 926.295
482 | 968.263 | 924.888
484 | 970.384 | 919.044
486 | 964.636 | 911.164
488 | 956.631 | 903.893
490 | 947.426 | 901.953
492 | 941.72 | 900.198
494 | 935.985 | 904.177
496 | 930.475 | 912.253
498 | 927.611 | 915.297
500 | 931.256 | 919.629
502 | 920.044
504 | 911.78
506 | 907.989
508 | 907.289
510 | 900.577
512 | 902.112
514 | 900.179
516 | 903.811
518 | 910.027
520 | 911.131 |  | End

## Profile data
Longitudinal profile data - Botswana pipeline
| OPTION 1: Pipeline goes through Serule before joining to BPT1 | OPTION2: Pipeline goes directly to BPT1
CHAINAGE (km0 | NGL (m) | NGL (m) |  | Botswana 1
2 | 1069.018 | 1069.018 | Start | Botswana 2
4 | 1067.321 | 1067.321
6 | 1064.035 | 1064.035
8 | 1063.832 | 1063.832
10 | 1067.893 | 1067.893
12 | 1075.133 | 1075.133
14 | 1082.768 | 1082.768
16 | 1089.726 | 1089.726
18 | 1094.131 | 1094.131
20 | 1097.897 | 1097.897
22 | 1101.67 | 1101.67
24 | 1095.952 | 1095.952
26 | 1090.107 | 1090.107
28 | 1085.781 | 1085.781
30 | 1081.89 | 1081.89
32 | 1077.937 | 1077.937
34 | 1074.89 | 1074.89
36 | 1071.114 | 1071.114
38 | 1065.311 | 1065.311
40 | 1059.051 | 1059.051
42 | 1054.28 | 1054.28
44 | 1053.871 | 1053.871
46 | 1050.42 | 1050.42
48 | 1052.704 | 1052.704
50 | 1056.355 | 1056.355
52 | 1058.466 | 1058.466
54 | 1055.99 | 1055.99
56 | 1055.66 | 1055.66
58 | 1056.404 | 1056.404
60 | 1056.841 | 1056.841
62 | 1056.377 | 1056.377
64 | 1052.503 | 1052.503
66 | 1046.022 | 1046.022
68 | 1036.575 | 1036.575
70 | 1031.818 | 1031.818
72 | 1027.675 | 1027.675
74 | 1023.844 | 1023.844
76 | 1020.888 | 1020.888
78 | 1023.648 | 1023.648
80 | 1027.566 | 1027.566
82 | 1032.371 | 1032.371
84 | 1034.983 | 1034.983
86 | 1033.213 | 1033.213
88 | 1031.188 | 1031.188
90 | 1029.08 | 1029.08
92 | 1026.322 | 1026.322
94 | 1023.207 | 1023.207
96 | 1021.503 | 1021.503
98 | 1019.765 | 1019.765
100 | 1018.493 | 1018.493
102 | 1016.444 | 1016.444
104 | 1013.288 | 1013.288
106 | 1007.843 | 1007.843
108 | 1001.282 | 1001.282
110 | 996.609 | 996.609
112 | 992.999 | 992.999
114 | 993.639 | 993.639
116 | 994.611 | 994.611
118 | 995.751 | 995.751
120 | 996.479 | 996.479
122 | 996.147 | 996.147
124 | 992.094 | 992.094
126 | 985.623 | 985.623
128 | 977.759 | 977.759
130 | 969.772 | 969.772
132 | 981.785 | 981.785
134 | 991.458 | 991.458
136 | 987.77 | 987.77
138 | 982.725 | 982.725
140 | 977.559 | 977.559
142 | 975.289 | 975.289
144 | 973.968 | 973.968
146 | 962.473 | 962.473
148 | 951.285 | 951.285
150 | 948.174 | 948.174
152 | 944.641 | 944.641
154 | 941.566 | 941.566
156 | 940.942 | 940.942
158 | 939.726 | 939.726
160 | 936.738 | 936.738
162 | 933.65 | 933.65
164 | 932.745 | 932.745
166 | 931.696 | 931.696
168 | 930.999 | 930.999
170 | 930.885 | 930.885
172 | 930.378 | 930.378
174 | 931.324 | 931.324
176 | 933.53 | 933.53
178 | 932.714 | 932.714
180 | 928.311 | 928.311
182 | 924.179 | 924.179
184 | 928.398 | 928.398
186 | 930.866 | 930.866
188 | 928.411 | 928.411
190 | 927.849 | 927.849
192 | 926.71 | 926.71
194 | 926.201 | 926.201
196 | 924.509 | 924.509
198 | 923.417 | 923.417
200 | 923.011 | 923.011
202 | 921.969 | 921.969
204 | 920.661 | 920.661
206 | 920.243 | 920.243
208 | 919.297 | 919.297
210 | 917.533 | 917.533
212 | 917.684 | 917.684
214 | 915.724 | 915.724
216 | 915.73 | 915.73
218 | 915.584 | 915.584
220 | 915.444 | 915.444
222 | 913.52 | 913.52
224 | 912.524 | 912.524
226 | 912.565 | 912.565
228 | 913.484 | 913.484
230 | 913.545 | 913.545
232 | 914.546 | 914.546
234 | 918.285 | 918.285
236 | 919.357 | 919.357
238 | 918.649 | 918.649
240 | 922.974 | 922.974
242 | 927.375 | 927.375
244 | 929.253 | 929.253
246 | 930.863 | 930.863
248 | 931.924 | 931.924
250 | 936.722 | 936.722
252 | 941.777 | 941.777
254 | 948.143 | 948.143
256 | 955.417 | 955.417
258 | 962.7 | 962.7
260 | 969.281 | 969.281
262 | 980.284 | 980.284
264 | 986.551 | 986.551
266 | 989.198 | 989.198
268 | 994.39 | 994.39
270 | 999.917 | 999.917
272 | 1004.623 | 1004.623
274 | 1008.819 | 1008.819
276 | 1007.834 | 1007.834
278 | 1005.626 | 1005.626
280 | 1001.623 | 1001.623
282 | 1004.052 | 1004.052
284 | 1010.797 | 1010.797
286 | 1014.67 | 1014.67
288 | 1017.319 | 1017.319
290 | 1027.459 | 1027.459
292 | 1031.99 | 1031.99
294 | 1036.254 | 1036.254
296 | 1040.127 | 1040.127
298 | 1044.396 | 1044.396
300 | 1051.339 | 1051.339
302 | 1060.955 | 1060.955
304 | 1070.227 | 1070.227
306 | 1072.691 | 1072.691
308 | 1076.503 | 1076.503
310 | 1083.996 | 1083.996
312 | 1097.188 | 1097.188
314 | 1103.545 | 1103.545
316 | 1105.174 | 1105.174
318 | 1111.657 | 1111.657
320 | 1122.935 | 1122.935
322 | 1128.197 | 1128.197
324 | 1132.561 | 1132.561
326 | 1131.854 | 1131.854
328 | 1133.338 | 1133.338
330 | 1136.405 | 1136.405
332 | 1128.709 | 1128.709
334 | 1120.713 | 1120.713
336 | 1115.226 | 1115.226
338 | 1108.709 | 1108.709
340 | 1102.499 | 1102.499
342 | 1096.349 | 1096.349
344 | 1090.39 | 1090.39
346 | 1087.765 | 1087.765
348 | 1084.661 | 1084.661
350 | 1081.662 | 1081.662
352 | 1076.872 | 1076.872
354 | 1070.898 | 1070.898
356 | 1065.018 | 1065.018
358 | 1059.58 | 1059.58
360 | 1055.284 | 1055.284
362 | 1050.886 | 1050.886
364 | 1052.647 | 1052.647
366 | 1051.117 | 1051.117
368 | 1048.266 | 1048.266
370 | 1040.172 | 1040.172
372 | 1033.483 | 1033.483
374 | 1030.95 | 1030.95
376 | 1032.263 | 1032.263
378 | 1031.391 | 1031.391
380 | 1025.791 | 1025.791
382 | 1020.911 | 1020.911
384 | 1015.65 | 1015.65
386 | 1012.139 | 1012.139
388 | 1010.472 | 1010.472
390 | 1005.401 | 1005.401
392 | 996.666 | 996.666
394 | 991.35 | 991.35
396 | 990.486 | 990.486
398 | 992.761 | 992.761
400 | 999.077 | 999.077
402 | 1001.8 | 1001.8
404 | 1002.224 | 1002.224
406 | 1002.003 | 1002.003
408 | 1003.596 | 1003.596
410 | 994.111 | 994.111
412 | 983.925 | 983.925
414 | 972.347 | 972.347
416 | 963.901 | 963.901
418 | 963.258 | 963.258
420 | 965.836 | 965.872
422 | 966.309 | 966.177
424 | 972.884 | 973.825
426 | 983.972 | 983.972
428 | 994.096 | 994.096
430 | 991.695 | 991.695
432 | 984.933 | 984.933
434 | 978.185 | 974.509
436 | 972.686 | 966.698
438 | 966.824 | 963.618
440 | 960.902 | 957.803
442 | 952.924 | 954.277
444 | 945.683 | 947.182
446 | 941.042 | 938.045
448 | 937.104 | 930.871
450 | 939.943 | 926.391
452 | 944.776 | 918.344
454 | 947.762 | 911.505
456 | 952.649 | 903.61
458 | 954.554 | 900.63
460 | 952.37 | 904.066
462 | 947.552 | 915.092
464 | 941.898 | 905.556
466 | 940.521 | 905.271
468 | 939.702 | 901.918
470 | 937.147 | 895.651
472 | 933.872 | 892.304
474 | 933.184 | 895.279
476 | 939.292 | 896.818
478 | 944.619 | 909.921
480 | 954.023 | 926.295
482 | 968.263 | 924.888
484 | 970.384 | 919.044
486 | 964.636 | 911.164
488 | 956.631 | 903.893
490 | 947.426 | 901.953
492 | 941.72 | 900.198
494 | 935.985 | 904.177
496 | 930.475 | 912.253
498 | 927.611 | 915.297
500 | 931.256 | 919.629
502 | 920.044
504 | 911.78
506 | 907.989
508 | 907.289
510 | 900.577
512 | 902.112
514 | 900.179
516 | 903.811
518 | 910.027
520 | 911.131 |  | End

## Flow Rate Calculations
Estimated Transfer Rate Demand | 100 | Mm3/a
Availible Days | 365
Pumping Hours | 24
Pf | 1.052
Pl | 1.02
PR | 1.2
Peak Design Flow | 4.0831 | m3/s

## Calculation Constants
Friction Factors
Ks (mm) - New | 0.03
Ks (mm) - Average | 0.06
Ks (mm) - Old | 0.15
Ks (mm) - Biofilm | 0.5
Kinemeatic Viscosity | 1.13e-06 | m2/s
Minor Loss - k | 150
Grade of Steel | X42
Yeild Capacity | 300 | Mpa
Design % of Yeild | 50%
Minimum D/t ratio | 160 | mm/mm

## Hydraulics
Option 4A |  |  |  | Option 4A | [12 empty] | Option 4A
Pump Station |  |  |  | Pipe Line | [9 empty] | Steel Pipeline Design |  |  | New Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Average Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Old Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Biofilm Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes
Name | Chainage (km) | Elevation (m) | Pumped Head (m) | Reference | Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Flow Rate (m3/s) | PipeVelocity (m/s) | Re | Static Head (m) | Dynamic Head (m) | Design Pressure (m) | Pipe Wall thickness (mm) | Steel Mass (kg) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m)
PS 1 | 8 | 1063.832 | 50 | Reservoir | 2 | 1069.018 | 0 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 10 | 10 | 10 | 11.875 | 0 | 0.00867 |  |  | 0 | 0 | 10 | 1079.018 | 0.0097304 |  |  | 0 | 0 | 10 | 1079.018 | 0.011459 |  |  | 0 | 0 | 10 | 1079.018 | 0.014543 |  |  | 0 | 0 | 10 | 1079.018
PS 3 | 228 | 913.484 | 260 |  | 4 | 1067.321 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 11.697 | 10.6713 | 11.697 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 10.6713 | 1077.9923 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 10.5534 | 1077.8744 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 10.361 | 1077.682 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 10.011 | 1077.332
[5 empty] | 6 | 1064.035 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 14.983 | 12.9317 | 14.983 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 12.9317 | 1076.9667 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 12.6957 | 1076.7307 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 12.311 | 1076.346 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 11.6111 | 1075.6461
|  |  |  | Pump Station | 8 | 1063.832 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 62.109 | 61.7551 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 50 | 62.109 | 1125.941 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 50 | 61.7551 | 1125.5871 | 0.011459 | 1.275 | 0.060983 | 1.336 | 50 | 61.1781 | 1125.0101 | 0.014543 | 1.625 | 0.060983 | 1.686 | 50 | 60.1281 | 1123.9601
[5 empty] | 10 | 1067.893 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 57.0224 | 56.5504 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 57.0224 | 1124.9154 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 56.5504 | 1124.4434 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 55.7811 | 1123.6741 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 54.3812 | 1122.2742
Reservoirs |  |  |  |  | 12 | 1075.133 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 48.7567 | 48.1668 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 48.7567 | 1123.8897 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 48.1668 | 1123.2998 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 47.2051 | 1122.3381 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 45.4552 | 1120.5882
Name | Chainage (km) | Water Elevation (m) | Height |  | 14 | 1082.768 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 40.096 | 39.3881 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 40.096 | 1122.864 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 39.3881 | 1122.1561 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 38.2341 | 1121.0021 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 36.1343 | 1118.9023
Supply Resrvoir | 2 | 1079.018 | 10 |  | 16 | 1089.726 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 32.1124 | 31.2865 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 32.1124 | 1121.8384 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 31.2865 | 1121.0125 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 29.9401 | 1119.6661 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.4903 | 1117.2163
BPT 3 | 22 | 1111.67 | 10 |  | 18 | 1094.131 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 26.6817 | 25.7378 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 26.6817 | 1120.8127 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 25.7378 | 1119.8688 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 24.1991 | 1118.3301 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 21.3994 | 1115.5304
BPT 5 | 228 | 923.484 | 10 |  | 20 | 1097.897 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 21.8901 | 20.8282 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 21.8901 | 1119.7871 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 20.8282 | 1118.7252 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 19.0972 | 1116.9942 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 15.9474 | 1113.8444
BPT 1 | 520 | 921.131 | 10 | Reservoir | 22 | 1101.67 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 10 | 10 | 10 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 10 | 1111.67 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 10 | 1111.67 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 10 | 1111.67 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 10 | 1111.67
[5 empty] | 24 | 1095.952 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 15.718 | 14.6923 | 15.718 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 14.6923 | 1110.6443 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 14.5744 | 1110.5264 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 14.382 | 1110.334 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 14.032 | 1109.984
[5 empty] | 26 | 1090.107 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 21.563 | 19.5117 | 21.563 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 19.5117 | 1109.6187 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 19.2757 | 1109.3827 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 18.891 | 1108.998 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 18.1911 | 1108.2981
|  | 188.186 |  |  | 28 | 1085.781 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 25.889 | 22.812 | 25.889 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 22.812 | 1108.593 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 22.4581 | 1108.2391 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 21.8811 | 1107.6621 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 20.8311 | 1106.6121
[5 empty] | 30 | 1081.89 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 29.78 | 25.6774 | 29.78 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 25.6774 | 1107.5674 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 25.2054 | 1107.0954 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 24.4361 | 1106.3261 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 23.0362 | 1104.9262
[5 empty] | 32 | 1077.937 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 33.733 | 28.6047 | 33.733 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 28.6047 | 1106.5417 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 28.0148 | 1105.9518 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 27.0531 | 1104.9901 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 25.3032 | 1103.2402
[5 empty] | 34 | 1074.89 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 36.78 | 30.626 | 36.78 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 30.626 | 1105.516 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 29.9181 | 1104.8081 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 28.7641 | 1103.6541 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 26.6643 | 1101.5543
[5 empty] | 36 | 1071.114 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 40.556 | 33.3764 | 40.556 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 33.3764 | 1104.4904 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 32.5505 | 1103.6645 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 31.2041 | 1102.3181 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 28.7543 | 1099.8683
Route | Botswana 1 |  |  |  | 38 | 1065.311 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 46.359 | 38.1537 | 46.359 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 38.1537 | 1103.4647 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 37.2098 | 1102.5208 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 35.6711 | 1100.9821 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 32.8714 | 1098.1824
Option | 4A |  |  |  | 40 | 1059.051 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 52.619 | 43.3881 | 52.619 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 43.3881 | 1102.4391 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 42.3262 | 1101.3772 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 40.5952 | 1099.6462 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 37.4454 | 1096.4964
[5 empty] | 42 | 1054.28 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 57.39 | 47.1334 | 57.39 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 47.1334 | 1101.4134 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 45.9535 | 1100.2335 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 44.0302 | 1098.3102 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 40.5304 | 1094.8104
[5 empty] | 44 | 1053.871 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 57.799 | 46.5167 | 57.799 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 46.5167 | 1100.3877 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 45.2189 | 1099.0899 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 43.1032 | 1096.9742 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 39.2535 | 1093.1245
[5 empty] | 46 | 1050.42 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 61.25 | 48.9421 | 61.25 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 48.9421 | 1099.3621 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 47.5263 | 1097.9463 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 45.2182 | 1095.6382 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 41.0185 | 1091.4385
[5 empty] | 48 | 1052.704 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 58.966 | 45.6324 | 58.966 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 45.6324 | 1098.3364 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 44.0986 | 1096.8026 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 41.5982 | 1094.3022 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 37.0486 | 1089.7526
[5 empty] | 50 | 1056.355 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.315 | 40.9557 | 55.315 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 40.9557 | 1097.3107 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 39.304 | 1095.659 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 36.6113 | 1092.9663 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 31.7116 | 1088.0666
[5 empty] | 52 | 1058.466 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 53.204 | 37.8191 | 53.204 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 37.8191 | 1096.2851 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 36.0493 | 1094.5153 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 33.1643 | 1091.6303 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.9147 | 1086.3807
[5 empty] | 54 | 1055.99 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.68 | 39.2694 | 55.68 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 39.2694 | 1095.2594 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 37.3817 | 1093.3717 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 34.3043 | 1090.2943 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 28.7047 | 1084.6947
[5 empty] | 56 | 1055.66 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 56.01 | 38.5738 | 56.01 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 38.5738 | 1094.2338 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 36.568 | 1092.228 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 33.2983 | 1088.9583 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.3488 | 1083.0088
[5 empty] | 58 | 1056.404 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.266 | 36.8041 | 55.266 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 36.8041 | 1093.2081 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 34.6804 | 1091.0844 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 31.2183 | 1087.6223 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 24.9188 | 1081.3228
[5 empty] | 60 | 1056.841 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 54.829 | 35.3414 | 54.829 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 35.3414 | 1092.1824 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 33.0997 | 1089.9407 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 29.4453 | 1086.2863 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 22.7958 | 1079.6368
[5 empty] | 62 | 1056.377 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.293 | 34.7798 | 55.293 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 34.7798 | 1091.1568 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 32.4201 | 1088.7971 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 28.5734 | 1084.9504 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 21.5739 | 1077.9509
[5 empty] | 64 | 1052.503 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 59.167 | 37.6281 | 59.167 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 37.6281 | 1090.1311 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 35.1504 | 1087.6534 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 31.1114 | 1083.6144 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 23.7619 | 1076.2649
[5 empty] | 66 | 1046.022 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 65.648 | 43.0835 | 65.648 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 43.0835 | 1089.1055 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 40.4878 | 1086.5098 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 36.2564 | 1082.2784 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 28.557 | 1074.579
[5 empty] | 68 | 1036.575 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 75.095 | 51.5048 | 75.095 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 51.5048 | 1088.0798 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 48.7911 | 1085.3661 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 44.3674 | 1080.9424 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 36.318 | 1072.893
[5 empty] | 70 | 1031.818 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 79.852 | 55.2361 | 79.852 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 55.2361 | 1087.0541 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 52.4045 | 1084.2225 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 47.7884 | 1079.6064 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 39.3891 | 1071.2071
[5 empty] | 72 | 1027.675 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 83.995 | 58.3535 | 83.995 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 58.3535 | 1086.0285 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 55.4039 | 1083.0789 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 50.5955 | 1078.2705 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 41.8461 | 1069.5211
[5 empty] | 74 | 1023.844 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 87.826 | 61.1588 | 87.826 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 61.1588 | 1085.0028 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 58.0912 | 1081.9352 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 53.0905 | 1076.9345 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 43.9912 | 1067.8352
[5 empty] | 76 | 1020.888 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 90.782 | 63.0892 | 90.782 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 63.0892 | 1083.9772 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 59.9036 | 1080.7916 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 54.7105 | 1075.5985 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 45.2612 | 1066.1492
[5 empty] | 78 | 1023.648 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 88.022 | 59.3035 | 88.022 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 59.3035 | 1082.9515 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 55.9999 | 1079.6479 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 50.6145 | 1074.2625 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 40.8152 | 1064.4632
[5 empty] | 80 | 1027.566 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 84.104 | 54.3598 | 84.104 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 54.3598 | 1081.9258 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 50.9383 | 1078.5043 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 45.3605 | 1072.9265 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 35.2113 | 1062.7773
[5 empty] | 82 | 1032.371 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 79.299 | 48.5292 | 79.299 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 48.5292 | 1080.9002 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 44.9896 | 1077.3606 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 39.2195 | 1071.5905 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 28.7203 | 1061.0913
[5 empty] | 84 | 1034.983 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 76.687 | 44.8915 | 76.687 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 44.8915 | 1079.8745 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 41.234 | 1076.217 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 35.2716 | 1070.2546 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 24.4224 | 1059.4054
[5 empty] | 86 | 1033.213 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 78.457 | 45.6358 | 78.457 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 45.6358 | 1078.8488 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 41.8603 | 1075.0733 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 35.7056 | 1068.9186 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 24.5064 | 1057.7194
[5 empty] | 88 | 1031.188 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 80.482 | 46.6352 | 80.482 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 46.6352 | 1077.8232 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 42.7417 | 1073.9297 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 36.3946 | 1067.5826 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 24.8455 | 1056.0335
[5 empty] | 90 | 1029.08 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 82.59 | 47.7175 | 82.59 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 47.7175 | 1076.7975 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 43.706 | 1072.786 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 37.1666 | 1066.2466 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 25.2675 | 1054.3475
[5 empty] | 92 | 1026.322 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 85.348 | 49.4499 | 85.348 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 49.4499 | 1075.7719 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 45.3204 | 1071.6424 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 38.5886 | 1064.9106 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 26.3395 | 1052.6615
[5 empty] | 94 | 1023.207 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 88.463 | 51.5392 | 88.463 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 51.5392 | 1074.7462 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 47.2918 | 1070.4988 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 40.3677 | 1063.5747 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.7686 | 1050.9756
[5 empty] | 96 | 1021.503 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 90.167 | 52.2175 | 90.167 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 52.2175 | 1073.7205 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 47.8521 | 1069.3551 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 40.7357 | 1062.2387 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.7866 | 1049.2896
[5 empty] | 98 | 1019.765 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 91.905 | 52.9299 | 91.905 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 52.9299 | 1072.6949 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 48.4465 | 1068.2115 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 41.1377 | 1060.9027 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.8387 | 1047.6037
[5 empty] | 100 | 1018.493 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 93.177 | 53.1762 | 93.177 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 53.1762 | 1071.6692 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 48.5748 | 1067.0678 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 41.0737 | 1059.5667 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.4247 | 1045.9177
[5 empty] | 102 | 1016.444 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 95.226 | 54.1996 | 95.226 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 54.1996 | 1070.6436 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 49.4802 | 1065.9242 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 41.7867 | 1058.2307 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.7878 | 1044.2318
[5 empty] | 104 | 1013.288 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 98.382 | 56.3299 | 98.382 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 56.3299 | 1069.6179 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 51.4925 | 1064.7805 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 43.6068 | 1056.8948 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 29.2578 | 1042.5458
[5 empty] | 106 | 1007.843 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 103.827 | 60.7492 | 103.827 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 60.7492 | 1068.5922 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 55.7939 | 1063.6369 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 47.7158 | 1055.5588 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 33.0169 | 1040.8599
[5 empty] | 108 | 1001.282 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 110.388 | 66.2846 | 110.388 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 66.2846 | 1067.5666 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 61.2112 | 1062.4932 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 52.9408 | 1054.2228 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 37.8919 | 1039.1739
[5 empty] | 110 | 996.609 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.061 | 69.9319 | 115.061 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 69.9319 | 1066.5409 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 64.7406 | 1061.3496 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 56.2778 | 1052.8868 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 40.8789 | 1037.4879
[5 empty] | 112 | 992.999 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 118.671 | 72.5163 | 118.671 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 72.5163 | 1065.5153 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 67.2069 | 1060.2059 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 58.5518 | 1051.5508 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 42.803 | 1035.802
[5 empty] | 114 | 993.639 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 118.031 | 70.8506 | 118.031 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 70.8506 | 1064.4896 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 65.4233 | 1059.0623 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 56.5758 | 1050.2148 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 40.477 | 1034.116
[5 empty] | 116 | 994.611 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 117.059 | 68.8529 | 117.059 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 68.8529 | 1063.4639 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 63.3077 | 1057.9187 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 54.2679 | 1048.8789 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 37.8191 | 1032.4301
[5 empty] | 118 | 995.751 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.919 | 66.6873 | 115.919 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 66.6873 | 1062.4383 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 61.024 | 1056.775 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 51.7919 | 1047.5429 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 34.9931 | 1030.7441
[5 empty] | 120 | 996.479 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.191 | 64.9336 | 115.191 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 64.9336 | 1061.4126 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 59.1524 | 1055.6314 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 49.7279 | 1046.2069 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 32.5792 | 1029.0582
[5 empty] | 122 | 996.147 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.523 | 64.2399 | 115.523 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 64.2399 | 1060.3869 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 58.3407 | 1054.4877 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 48.7239 | 1044.8709 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 31.2252 | 1027.3722
[5 empty] | 124 | 992.094 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 119.576 | 67.2673 | 119.576 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 67.2673 | 1059.3613 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 61.2501 | 1053.3441 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 51.4409 | 1043.5349 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 33.5923 | 1025.6863
[5 empty] | 126 | 985.623 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 126.047 | 72.7126 | 126.047 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 72.7126 | 1058.3356 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 66.5774 | 1052.2004 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 56.576 | 1042.199 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 38.3773 | 1024.0003
[5 empty] | 128 | 977.759 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 133.911 | 79.551 | 133.911 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 79.551 | 1057.31 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 73.2978 | 1051.0568 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 63.104 | 1040.863 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 44.5553 | 1022.3143
[5 empty] | 130 | 969.772 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 141.898 | 86.5123 | 141.898 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 86.5123 | 1056.2843 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 80.1411 | 1049.9131 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 69.755 | 1039.527 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 50.8564 | 1020.6284
[5 empty] | 132 | 981.785 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 129.885 | 73.4736 | 129.885 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 73.4736 | 1055.2586 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 66.9845 | 1048.7695 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 56.406 | 1038.191 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 37.1574 | 1018.9424
[5 empty] | 134 | 991.458 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 120.212 | 62.775 | 120.212 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 62.775 | 1054.233 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 56.1678 | 1047.6258 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 45.397 | 1036.855 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 25.7985 | 1017.2565
[5 empty] | 136 | 987.77 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 123.9 | 65.4373 | 123.9 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 65.4373 | 1053.2073 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 58.7122 | 1046.4822 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 47.749 | 1035.519 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.8005 | 1015.5705
[5 empty] | 138 | 982.725 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 128.945 | 69.4567 | 128.945 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 69.4567 | 1052.1817 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 62.6136 | 1045.3386 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 51.4581 | 1034.1831 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 31.1596 | 1013.8846
[5 empty] | 140 | 977.559 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 134.111 | 73.597 | 134.111 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 73.597 | 1051.156 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 66.6359 | 1044.1949 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 55.2881 | 1032.8471 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 34.6396 | 1012.1986
[5 empty] | 142 | 975.289 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 136.381 | 74.8413 | 136.381 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 74.8413 | 1050.1303 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 67.7623 | 1043.0513 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 56.2221 | 1031.5111 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 35.2237 | 1010.5127
[5 empty] | 144 | 973.968 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 137.702 | 75.1367 | 137.702 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 75.1367 | 1049.1047 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 67.9396 | 1041.9076 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 56.2071 | 1030.1751 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 34.8587 | 1008.8267
[5 empty] | 146 | 962.473 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 149.197 | 85.606 | 149.197 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 85.606 | 1048.079 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 78.291 | 1040.764 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 66.3661 | 1028.8391 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 44.6677 | 1007.1407
[5 empty] | 148 | 951.285 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 160.385 | 95.7684 | 160.385 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 95.7684 | 1047.0534 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 88.3353 | 1039.6203 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 76.2182 | 1027.5032 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 54.1698 | 1005.4548
[5 empty] | 150 | 948.174 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 163.496 | 97.8537 | 163.496 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 97.8537 | 1046.0277 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 90.3027 | 1038.4767 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 77.9932 | 1026.1672 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 55.5948 | 1003.7688
[5 empty] | 152 | 944.641 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 167.029 | 100.361 | 167.029 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 100.361 | 1045.002 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 92.692 | 1037.333 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 80.1902 | 1024.8312 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 57.4419 | 1002.0829
[5 empty] | 154 | 941.566 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 170.104 | 102.4104 | 170.104 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 102.4104 | 1043.9764 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 94.6234 | 1036.1894 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 81.9292 | 1023.4952 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 58.8309 | 1000.3969
[5 empty] | 156 | 940.942 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 170.728 | 102.0087 | 170.728 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 102.0087 | 1042.9507 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 94.1037 | 1035.0457 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 81.2172 | 1022.1592 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 57.769 | 998.711
[5 empty] | 158 | 939.726 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 171.944 | 101.8738 | 171.944 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 101.8738 | 1041.5998 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 93.8121 | 1033.5381 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 80.6698 | 1020.3958 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 56.7549 | 996.4809
[5 empty] | 160 | 936.738 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 174.932 | 103.5108 | 174.932 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 103.5108 | 1040.2488 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 95.2924 | 1032.0304 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 81.8944 | 1018.6324 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 57.5129 | 994.2509
[5 empty] | 162 | 933.65 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.02 | 105.2478 | 178.02 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 105.2478 | 1038.8978 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 96.8727 | 1030.5227 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 83.219 | 1016.869 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 58.3709 | 992.0209
[5 empty] | 164 | 932.745 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.925 | 104.8019 | 178.925 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 104.8019 | 1037.5469 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 96.2701 | 1029.0151 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 82.3606 | 1015.1056 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 57.0459 | 989.7909
[5 empty] | 166 | 931.696 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 179.974 | 104.4999 | 179.974 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 104.4999 | 1036.1959 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 95.8114 | 1027.5074 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 81.6462 | 1013.3422 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.8649 | 987.5609
[5 empty] | 168 | 930.999 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.671 | 103.846 | 180.671 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 103.846 | 1034.845 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 95.0007 | 1025.9997 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 80.5798 | 1011.5788 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 54.3319 | 985.3309
[5 empty] | 170 | 930.885 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.785 | 102.609 | 180.785 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 102.609 | 1033.494 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 93.6071 | 1024.4921 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 78.9304 | 1009.8154 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 52.2159 | 983.1009
[5 empty] | 172 | 930.378 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 181.292 | 101.7651 | 181.292 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 101.7651 | 1032.1431 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 92.6064 | 1022.9844 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 77.6741 | 1008.0521 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 50.4928 | 980.8708
[5 empty] | 174 | 931.324 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.346 | 99.4681 | 180.346 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 99.4681 | 1030.7921 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 90.1527 | 1021.4767 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 74.9647 | 1006.2887 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 47.3168 | 978.6408
[5 empty] | 176 | 933.53 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.14 | 95.9112 | 178.14 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 95.9112 | 1029.4412 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 86.439 | 1019.969 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 70.9953 | 1004.5253 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 42.8808 | 976.4108
[5 empty] | 178 | 932.714 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.956 | 95.3762 | 178.956 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 95.3762 | 1028.0902 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 85.7474 | 1018.4614 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 70.0479 | 1002.7619 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 41.4668 | 974.1808
[5 empty] | 180 | 928.311 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.359 | 98.4283 | 183.359 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 98.4283 | 1026.7393 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 88.6427 | 1016.9537 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 72.6875 | 1000.9985 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 43.6398 | 971.9508
[5 empty] | 182 | 924.179 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 187.491 | 101.2093 | 187.491 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 101.2093 | 1025.3883 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 91.267 | 1015.446 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 75.0561 | 999.2351 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 45.5418 | 969.7208
[5 empty] | 184 | 928.398 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.272 | 95.6394 | 183.272 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 95.6394 | 1024.0374 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 85.5404 | 1013.9384 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 69.0737 | 997.4717 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 39.0927 | 967.4907
[5 empty] | 186 | 930.866 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.804 | 91.8204 | 180.804 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 91.8204 | 1022.6864 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 81.5647 | 1012.4307 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 64.8423 | 995.7083 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 34.3947 | 965.2607
[5 empty] | 188 | 928.411 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.259 | 92.9244 | 183.259 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 92.9244 | 1021.3354 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 82.512 | 1010.923 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 65.5339 | 993.9449 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 34.6197 | 963.0307
[5 empty] | 190 | 927.849 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.821 | 92.1355 | 183.821 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 92.1355 | 1019.9845 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 81.5664 | 1009.4154 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 64.3325 | 992.1815 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 32.9517 | 960.8007
[5 empty] | 192 | 926.71 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 184.96 | 91.9235 | 184.96 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 91.9235 | 1018.6335 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 81.1977 | 1007.9077 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 63.7081 | 990.4181 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 31.8607 | 958.5707
[5 empty] | 194 | 926.201 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 185.469 | 91.0816 | 185.469 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 91.0816 | 1017.2826 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 80.199 | 1006.4 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 62.4537 | 988.6547 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 30.1397 | 956.3407
[5 empty] | 196 | 924.509 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 187.161 | 91.4226 | 187.161 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 91.4226 | 1015.9316 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 80.3834 | 1004.8924 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 62.3823 | 986.8913 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 29.6016 | 954.1106
[5 empty] | 198 | 923.417 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 188.253 | 91.1637 | 188.253 | 11.2952 | 996509.3057 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 91.1637 | 1014.5807 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 79.9677 | 1003.3847 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 61.7109 | 985.1279 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 28.4636 | 951.8806
[5 empty] | 200 | 923.011 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 188.659 | 90.2187 | 188.659 | 11.3195 | 998644.849 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 90.2187 | 1013.2297 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 78.866 | 1001.877 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 60.3535 | 983.3645 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 26.6396 | 949.6506
[5 empty] | 202 | 921.969 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 189.701 | 89.9098 | 189.701 | 11.3821 | 1004125.4583 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 89.9098 | 1011.8788 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 78.4003 | 1000.3693 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 59.6321 | 981.6011 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 25.4516 | 947.4206
[5 empty] | 204 | 920.661 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 191.009 | 89.8668 | 191.009 | 11.4605 | 1011004.6025 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 89.8668 | 1010.5278 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 78.2007 | 998.8617 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 59.1767 | 979.8377 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 24.5296 | 945.1906
[5 empty] | 206 | 920.243 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 191.427 | 88.9339 | 191.427 | 11.4856 | 1013202.8554 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 88.9339 | 1009.1769 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 77.111 | 997.354 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 57.8313 | 978.0743 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 22.7176 | 942.9606
[5 empty] | 208 | 919.297 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 192.373 | 88.5289 | 192.373 | 11.5424 | 1018177.6195 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 88.5289 | 1007.8259 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 76.5493 | 995.8463 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 57.0139 | 976.3109 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 21.4335 | 940.7305
[5 empty] | 210 | 917.533 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 194.137 | 88.942 | 194.137 | 11.6482 | 1027453.1808 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 88.942 | 1006.475 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 76.8057 | 994.3387 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 57.0145 | 974.5475 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 20.9675 | 938.5005
[5 empty] | 212 | 917.684 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 193.986 | 87.44 | 193.986 | 11.6392 | 1026659.2276 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 87.44 | 1005.124 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 75.147 | 992.831 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 55.1001 | 972.7841 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 18.5865 | 936.2705
[5 empty] | 214 | 915.724 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 195.946 | 88.049 | 195.946 | 11.7568 | 1036964.2159 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 88.049 | 1003.773 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 75.5993 | 991.3233 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 55.2967 | 971.0207 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 18.3165 | 934.0405
[5 empty] | 216 | 915.73 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 195.94 | 86.6921 | 195.94 | 11.7564 | 1036932.6721 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 86.6921 | 1002.4221 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 74.0857 | 989.8157 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 53.5273 | 969.2573 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 16.0805 | 931.8105
[5 empty] | 218 | 915.584 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 196.086 | 85.4871 | 196.086 | 11.7652 | 1037700.2343 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 85.4871 | 1001.0711 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 72.724 | 988.308 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 51.9099 | 967.4939 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 13.9965 | 929.5805
[5 empty] | 220 | 915.444 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 196.226 | 84.2762 | 196.226 | 11.7736 | 1038436.2457 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 84.2762 | 999.7202 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 71.3563 | 986.8003 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 50.2865 | 965.7305 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 11.9064 | 927.3504
[5 empty] | 222 | 913.52 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 198.15 | 84.8492 | 198.15 | 11.889 | 1048550.4405 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 84.8492 | 998.3692 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 71.7727 | 985.2927 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 50.4471 | 963.9671 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 11.6004 | 925.1204
[5 empty] | 224 | 912.524 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 199.146 | 84.4943 | 199.146 | 11.9488 | 1053785.7546 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 84.4943 | 997.0183 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 71.261 | 983.785 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 49.6797 | 962.2037 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 10.3664 | 922.8904
[5 empty] | 226 | 912.565 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 199.105 | 83.1023 | 199.105 | 11.9463 | 1053570.2516 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 83.1023 | 995.6673 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 69.7123 | 982.2773 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 47.8753 | 960.4403 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 8.0954 | 920.6604
|  |  |  | Reservoir | 228 | 913.484 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 10 | 270 | 19.8 | 2129173.4923 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 260 | 10 | 1183.484 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 260 | 270 | 1183.484 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 260 | 270 | 1183.484 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 260 | 270 | 1183.484
[5 empty] | 230 | 913.545 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 269.4524 | 269.3977 | 19.7558 | 2124467.1056 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 269.4524 | 1182.9974 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 269.3977 | 1182.9427 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 269.3089 | 1182.8539 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 269.1483 | 1182.6933
[5 empty] | 232 | 914.546 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 267.9648 | 267.8555 | 19.6427 | 2112414.3333 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 267.9648 | 1182.5108 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 267.8555 | 1182.4015 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 267.6777 | 1182.2237 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 267.3566 | 1181.9026
[5 empty] | 234 | 918.285 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 263.7392 | 263.5752 | 19.3288 | 2078957.6466 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 263.7392 | 1182.0242 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 263.5752 | 1181.8602 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 263.3086 | 1181.5936 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 262.8269 | 1181.1119
[5 empty] | 236 | 919.357 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 262.1805 | 261.9619 | 19.2105 | 2066345.0001 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 262.1805 | 1181.5375 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 261.9619 | 1181.3189 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 261.6064 | 1180.9634 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 260.9642 | 1180.3212
[5 empty] | 238 | 918.649 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 262.4019 | 262.1286 | 19.2228 | 2067648.5413 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 262.4019 | 1181.0509 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 262.1286 | 1180.7776 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 261.6843 | 1180.3333 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 260.8815 | 1179.5305
[5 empty] | 240 | 922.974 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 257.5903 | 257.2624 | 18.8659 | 2029595.8547 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 257.5903 | 1180.5643 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 257.2624 | 1180.2364 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 256.7291 | 1179.7031 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 255.7658 | 1178.7398
[5 empty] | 242 | 927.375 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 252.7027 | 252.3201 | 18.5035 | 1990936.0143 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 252.7027 | 1180.0777 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 252.3201 | 1179.6951 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 251.698 | 1179.073 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 250.5742 | 1177.9492
[5 empty] | 244 | 929.253 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 250.3381 | 249.9008 | 18.3261 | 1972007.0597 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 250.3381 | 1179.5911 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 249.9008 | 1179.1538 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 249.1899 | 1178.4429 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 247.9055 | 1177.1585
[5 empty] | 246 | 930.863 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 248.2415 | 247.7495 | 18.1683 | 1955172.3912 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 248.2415 | 1179.1045 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 247.7495 | 1178.6125 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 246.9497 | 1177.8127 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 245.5048 | 1176.3678
[5 empty] | 248 | 931.924 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 246.6939 | 246.1473 | 18.0508 | 1942632.2961 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 246.6939 | 1178.6179 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 246.1473 | 1178.0713 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 245.2586 | 1177.1826 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 243.6531 | 1175.5771
[5 empty] | 250 | 936.722 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 241.4092 | 240.808 | 17.6593 | 1900834.9656 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 241.4092 | 1178.1312 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 240.808 | 1177.53 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 239.8304 | 1176.5524 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 238.0644 | 1174.7864
[5 empty] | 252 | 941.777 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 235.8676 | 235.2117 | 17.2489 | 1857009.5342 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 235.8676 | 1177.6446 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 235.2117 | 1176.9887 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 234.1453 | 1175.9223 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 232.2187 | 1173.9957
[5 empty] | 254 | 948.143 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 229.015 | 228.3044 | 16.7423 | 1802894.5158 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 229.015 | 1177.158 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 228.3044 | 1176.4474 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 227.1491 | 1175.2921 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 225.062 | 1173.205
[5 empty] | 256 | 955.417 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 221.2544 | 220.4892 | 16.1692 | 1741635.2535 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 221.2544 | 1176.6714 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 220.4892 | 1175.9062 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 219.245 | 1174.662 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 216.9973 | 1172.4143
[5 empty] | 258 | 962.7 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 213.4848 | 212.6649 | 15.5954 | 1680272.9878 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 213.4848 | 1176.1848 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 212.6649 | 1175.3649 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 211.3319 | 1174.0319 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 208.9236 | 1171.6236
[5 empty] | 260 | 969.281 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 206.4172 | 205.5426 | 15.0731 | 1624387.9565 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 206.4172 | 1175.6982 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 205.5426 | 1174.8236 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 204.1207 | 1173.4017 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 201.5519 | 1170.8329
[5 empty] | 262 | 980.284 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 194.9276 | 193.9984 | 14.2265 | 1533748.4729 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 194.9276 | 1175.2116 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 193.9984 | 1174.2824 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 192.4876 | 1172.7716 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 189.7582 | 1170.0422
[5 empty] | 264 | 986.551 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 188.174 | 187.1901 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 188.174 | 1174.725 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 187.1901 | 1173.7411 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 185.5904 | 1172.1414 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 182.7005 | 1169.2515
[5 empty] | 266 | 989.198 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 185.0403 | 184.0018 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 185.0403 | 1174.2383 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 184.0018 | 1173.1998 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 182.3133 | 1171.5113 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 179.2628 | 1168.4608
[5 empty] | 268 | 994.39 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 179.3617 | 178.2685 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 179.3617 | 1173.7517 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 178.2685 | 1172.6585 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 176.4911 | 1170.8811 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 173.2802 | 1167.6702
[5 empty] | 270 | 999.917 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 173.3481 | 172.2003 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 173.3481 | 1173.2651 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 172.2003 | 1172.1173 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 170.334 | 1170.251 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 166.9625 | 1166.8795
[5 empty] | 272 | 1004.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 168.1555 | 166.953 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 168.1555 | 1172.7785 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 166.953 | 1171.576 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 164.9979 | 1169.6209 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 161.4658 | 1166.0888
[5 empty] | 274 | 1008.819 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 163.4729 | 162.2157 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 163.4729 | 1172.2919 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 162.2157 | 1171.0347 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 160.1717 | 1168.9907 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 156.4791 | 1165.2981
[5 empty] | 276 | 1007.834 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 163.9713 | 162.6594 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 163.9713 | 1171.8053 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 162.6594 | 1170.4934 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 160.5266 | 1168.3606 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 156.6734 | 1164.5074
[5 empty] | 278 | 1005.626 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 165.6927 | 164.3262 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 165.6927 | 1171.3187 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 164.3262 | 1169.9522 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 162.1044 | 1167.7304 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 158.0907 | 1163.7167
[5 empty] | 280 | 1001.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 169.209 | 167.7879 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 169.209 | 1170.832 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 167.7879 | 1169.4109 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 165.4773 | 1167.1003 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 161.303 | 1162.926
[5 empty] | 282 | 1004.052 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 166.2934 | 164.8176 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 166.2934 | 1170.3454 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 164.8176 | 1168.8696 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 162.4181 | 1166.4701 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 158.0833 | 1162.1353
[5 empty] | 284 | 1010.797 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 159.0618 | 157.5313 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 159.0618 | 1169.8588 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 157.5313 | 1168.3283 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 155.043 | 1165.84 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 150.5476 | 1161.3446
[5 empty] | 286 | 1014.67 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 154.7022 | 153.1171 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 154.7022 | 1169.3722 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 153.1171 | 1167.7871 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 150.5398 | 1165.2098 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 145.8839 | 1160.5539
[5 empty] | 288 | 1017.319 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 151.5666 | 149.9268 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 151.5666 | 1168.8856 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 149.9268 | 1167.2458 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 147.2607 | 1164.5797 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 142.4442 | 1159.7632
[5 empty] | 290 | 1027.459 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 140.94 | 139.2455 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 140.94 | 1168.399 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 139.2455 | 1166.7045 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 136.4906 | 1163.9496 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 131.5135 | 1158.9725
[5 empty] | 292 | 1031.99 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 135.9224 | 134.1733 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 135.9224 | 1167.9124 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 134.1733 | 1166.1633 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 131.3294 | 1163.3194 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 126.1918 | 1158.1818
[5 empty] | 294 | 1036.254 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 131.1717 | 129.368 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 131.1717 | 1167.4257 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 129.368 | 1165.622 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 126.4353 | 1162.6893 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 121.1372 | 1157.3912
[5 empty] | 296 | 1040.127 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 126.8121 | 124.9537 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 126.8121 | 1166.9391 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 124.9537 | 1165.0807 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 121.9321 | 1162.0591 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 116.4735 | 1156.6005
[5 empty] | 298 | 1044.396 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 122.0565 | 120.1434 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 122.0565 | 1166.4525 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 120.1434 | 1164.5394 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 117.033 | 1161.429 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 111.4138 | 1155.8098
[5 empty] | 300 | 1051.339 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 114.6269 | 112.6592 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 114.6269 | 1165.9659 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 112.6592 | 1163.9982 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 109.4598 | 1160.7988 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 103.6801 | 1155.0191
[5 empty] | 302 | 1060.955 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 104.5243 | 102.5019 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 104.5243 | 1165.4793 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 102.5019 | 1163.4569 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 99.2137 | 1160.1687 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 93.2734 | 1154.2284
[5 empty] | 304 | 1070.227 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 94.7657 | 92.6886 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 94.7657 | 1164.9927 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 92.6886 | 1162.9156 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 89.3116 | 1159.5386 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 83.2107 | 1153.4377
[5 empty] | 306 | 1072.691 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 91.8151 | 89.6833 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 91.8151 | 1164.5061 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 89.6833 | 1162.3743 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 86.2174 | 1158.9084 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 79.956 | 1152.647
[5 empty] | 308 | 1076.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 87.5164 | 85.3301 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 87.5164 | 1164.0194 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 85.3301 | 1161.8331 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 81.7753 | 1158.2783 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 75.3533 | 1151.8563
[5 empty] | 310 | 1083.996 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 79.5368 | 77.2958 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 79.5368 | 1163.5328 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 77.2958 | 1161.2918 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 73.6521 | 1157.6481 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 67.0696 | 1151.0656
[5 empty] | 312 | 1097.188 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 65.8582 | 63.5625 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 65.8582 | 1163.0462 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 63.5625 | 1160.7505 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 59.83 | 1157.018 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 53.0869 | 1150.2749
[5 empty] | 314 | 1103.545 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 59.0146 | 56.6642 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 59.0146 | 1162.5596 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 56.6642 | 1160.2092 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 52.8428 | 1156.3878 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 45.9392 | 1149.4842
[5 empty] | 316 | 1105.174 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 56.899 | 54.494 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 56.899 | 1162.073 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 54.494 | 1159.668 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 50.5837 | 1155.7577 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 43.5195 | 1148.6935
[5 empty] | 318 | 1111.657 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 49.9294 | 47.4697 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 49.9294 | 1161.5864 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 47.4697 | 1159.1267 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 43.4706 | 1155.1276 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 36.2458 | 1147.9028
[5 empty] | 320 | 1122.935 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 38.1648 | 35.6504 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 38.1648 | 1161.0998 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 35.6504 | 1158.5854 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 31.5624 | 1154.4974 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 24.1772 | 1147.1122
[5 empty] | 322 | 1128.197 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 32.4161 | 29.8472 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 32.4161 | 1160.6131 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 29.8472 | 1158.0442 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 25.6703 | 1153.8673 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 18.1245 | 1146.3215
[5 empty] | 324 | 1132.561 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 27.5655 | 24.9419 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 27.5655 | 1160.1265 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 24.9419 | 1157.5029 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 20.6761 | 1153.2371 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 12.9698 | 1145.5308
[5 empty] | 326 | 1131.854 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 27.7859 | 25.1076 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 27.7859 | 1159.6399 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 25.1076 | 1156.9616 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 20.753 | 1152.607 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 12.8861 | 1144.7401
[5 empty] | 328 | 1133.338 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 25.8153 | 23.0823 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 25.8153 | 1159.1533 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 23.0823 | 1156.4203 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 18.6388 | 1151.9768 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 10.6114 | 1143.9494
[5 empty] | 330 | 1136.405 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 22.2617 | 19.4741 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 22.2617 | 1158.6667 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 19.4741 | 1155.8791 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 14.9417 | 1151.3467 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 6.7537 | 1143.1587
[5 empty] | 332 | 1128.709 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 29.4711 | 26.6288 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 29.4711 | 1158.1801 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 26.6288 | 1155.3378 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 22.0076 | 1150.7166 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 13.659 | 1142.368
[5 empty] | 334 | 1120.713 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 36.9805 | 34.0835 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 36.9805 | 1157.6935 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 34.0835 | 1154.7965 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 29.3734 | 1150.0864 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 20.8643 | 1141.5773
[5 empty] | 336 | 1115.226 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 41.1165 | 38.0628 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 41.1165 | 1156.3425 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 38.0628 | 1153.2888 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 33.097 | 1148.323 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 24.1213 | 1139.3473
[5 empty] | 338 | 1108.709 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 46.2826 | 43.0722 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 46.2826 | 1154.9916 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 43.0722 | 1151.7812 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 37.8506 | 1146.5596 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 28.4083 | 1137.1173
[5 empty] | 340 | 1102.499 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 51.1416 | 47.7745 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 51.1416 | 1153.6406 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 47.7745 | 1150.2735 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 42.2972 | 1144.7962 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 32.3883 | 1134.8873
[5 empty] | 342 | 1096.349 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 55.9407 | 52.4168 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 55.9407 | 1152.2897 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 52.4168 | 1148.7658 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 46.6838 | 1143.0328 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 36.3082 | 1132.6572
[5 empty] | 344 | 1090.39 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 60.5487 | 56.8682 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 60.5487 | 1150.9387 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 56.8682 | 1147.2582 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 50.8794 | 1141.2694 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 40.0372 | 1130.4272
[5 empty] | 346 | 1087.765 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 61.8227 | 57.9855 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 61.8227 | 1149.5877 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 57.9855 | 1145.7505 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 51.741 | 1139.506 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 40.4322 | 1128.1972
[5 empty] | 348 | 1084.661 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 63.5758 | 59.5818 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 63.5758 | 1148.2368 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 59.5818 | 1144.2428 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 53.0816 | 1137.7426 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 41.3062 | 1125.9672
[5 empty] | 350 | 1081.662 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 65.2238 | 61.0732 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 65.2238 | 1146.8858 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 61.0732 | 1142.7352 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 54.3172 | 1135.9792 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 42.0752 | 1123.7372
[5 empty] | 352 | 1076.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 68.6629 | 64.3555 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 68.6629 | 1145.5349 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 64.3555 | 1141.2275 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 57.3438 | 1134.2158 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 44.6352 | 1121.5072
[5 empty] | 354 | 1070.898 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 73.2859 | 68.8218 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 73.2859 | 1144.1839 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 68.8218 | 1139.7198 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 61.5544 | 1132.4524 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 48.3791 | 1119.2771
[5 empty] | 356 | 1065.018 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 77.815 | 73.1942 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 77.815 | 1142.833 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 73.1942 | 1138.2122 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 65.6711 | 1130.6891 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 52.0291 | 1117.0471
[5 empty] | 358 | 1059.58 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 81.902 | 77.1245 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 81.902 | 1141.482 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 77.1245 | 1136.7045 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 69.3457 | 1128.9257 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.2371 | 1114.8171
[5 empty] | 360 | 1055.284 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 84.8471 | 79.9128 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 84.8471 | 1140.1311 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 79.9128 | 1135.1968 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 71.8783 | 1127.1623 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 57.3031 | 1112.5871
[5 empty] | 362 | 1050.886 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 87.8941 | 82.8031 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 87.8941 | 1138.7801 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 82.8031 | 1133.6891 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 74.5129 | 1125.3989 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 59.4711 | 1110.3571
[5 empty] | 364 | 1052.647 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 84.7822 | 79.5345 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 84.7822 | 1137.4292 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 79.5345 | 1132.1815 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 70.9885 | 1123.6355 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.4801 | 1108.1271
[5 empty] | 366 | 1051.117 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 84.9612 | 79.5568 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 84.9612 | 1136.0782 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 79.5568 | 1130.6738 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 70.7551 | 1121.8721 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 54.78 | 1105.897
[5 empty] | 368 | 1048.266 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 86.4613 | 80.9001 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 86.4613 | 1134.7273 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 80.9001 | 1129.1661 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 71.8427 | 1120.1087 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.401 | 1103.667
[5 empty] | 370 | 1040.172 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 93.2043 | 87.4865 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 93.2043 | 1133.3763 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 87.4865 | 1127.6585 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 78.1733 | 1118.3453 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 61.265 | 1101.437
[5 empty] | 372 | 1033.483 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 98.5423 | 92.6678 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 98.5423 | 1132.0253 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 92.6678 | 1126.1508 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 83.0989 | 1116.5819 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 65.724 | 1099.207
[5 empty] | 374 | 1030.95 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 99.7244 | 93.6931 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 99.7244 | 1130.6744 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 93.6931 | 1124.6431 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 83.8685 | 1114.8185 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 66.027 | 1096.977
[5 empty] | 376 | 1032.263 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 97.0604 | 90.8725 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 97.0604 | 1129.3234 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 90.8725 | 1123.1355 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 80.7921 | 1113.0551 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 62.484 | 1094.747
[5 empty] | 378 | 1031.391 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 96.5815 | 90.2368 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 96.5815 | 1127.9725 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 90.2368 | 1121.6278 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 79.9007 | 1111.2917 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 61.1259 | 1092.5169
[5 empty] | 380 | 1025.791 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 100.8305 | 94.3291 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 100.8305 | 1126.6215 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 94.3291 | 1120.1201 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 83.7373 | 1109.5283 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 64.4959 | 1090.2869
[5 empty] | 382 | 1020.911 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 104.3596 | 97.7015 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 104.3596 | 1125.2706 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 97.7015 | 1118.6125 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 86.8539 | 1107.7649 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 67.1459 | 1088.0569
[5 empty] | 384 | 1015.65 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 108.2696 | 101.4548 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 108.2696 | 1123.9196 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 101.4548 | 1117.1048 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 90.3515 | 1106.0015 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 70.1769 | 1085.8269
[5 empty] | 386 | 1012.139 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 110.4297 | 103.4581 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 110.4297 | 1122.5687 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 103.4581 | 1115.5971 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 92.0991 | 1104.2381 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 71.4579 | 1083.5969
[5 empty] | 388 | 1010.472 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 110.7457 | 103.6174 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 110.7457 | 1121.2177 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 103.6174 | 1114.0894 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 92.0027 | 1102.4747 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 70.8949 | 1081.3669
[5 empty] | 390 | 1005.401 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 114.4658 | 107.1808 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 114.4658 | 1119.8668 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 107.1808 | 1112.5818 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 95.3103 | 1100.7113 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 73.7358 | 1079.1368
[5 empty] | 392 | 996.666 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 121.8498 | 114.4081 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 121.8498 | 1118.5158 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 114.4081 | 1111.0741 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 102.2819 | 1098.9479 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 80.2408 | 1076.9068
[5 empty] | 394 | 991.35 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 125.8149 | 118.2164 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 125.8149 | 1117.1649 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 118.2164 | 1109.5664 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 105.8345 | 1097.1845 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 83.3268 | 1074.6768
[5 empty] | 396 | 990.486 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 125.3279 | 117.5728 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 125.3279 | 1115.8139 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 117.5728 | 1108.0588 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 104.9351 | 1095.4211 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 81.9608 | 1072.4468
[5 empty] | 398 | 992.761 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 121.7019 | 113.7901 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 121.7019 | 1114.4629 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 113.7901 | 1106.5511 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 100.8967 | 1093.6577 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 77.4558 | 1070.2168
[5 empty] | 400 | 999.077 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 114.035 | 105.9664 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 114.035 | 1113.112 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 105.9664 | 1105.0434 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 92.8173 | 1091.8943 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 68.9098 | 1067.9868
[5 empty] | 402 | 1001.8 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 109.961 | 101.7358 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 109.961 | 1111.761 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 101.7358 | 1103.5358 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 88.3309 | 1090.1309 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 63.9567 | 1065.7567
[5 empty] | 404 | 1002.224 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 108.1861 | 99.8041 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 108.1861 | 1110.4101 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 99.8041 | 1102.0281 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 86.1435 | 1088.3675 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 61.3027 | 1063.5267
[5 empty] | 406 | 1002.003 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 107.0561 | 98.5174 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 107.0561 | 1109.0591 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 98.5174 | 1100.5204 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 84.6011 | 1086.6041 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 59.2937 | 1061.2967
[5 empty] | 408 | 1003.596 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 104.1122 | 95.4168 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 104.1122 | 1107.7082 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 95.4168 | 1099.0128 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 81.2447 | 1084.8407 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.4707 | 1059.0667
[5 empty] | 410 | 994.111 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 112.2462 | 103.3941 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 112.2462 | 1106.3572 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 103.3941 | 1097.5051 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 88.9663 | 1083.0773 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 62.7257 | 1056.8367
[5 empty] | 412 | 983.925 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 121.0813 | 112.0724 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 121.0813 | 1105.0063 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 112.0724 | 1095.9974 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 97.3889 | 1081.3139 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 70.6817 | 1054.6067
[5 empty] | 414 | 972.347 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 131.3083 | 122.1427 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 131.3083 | 1103.6553 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 122.1427 | 1094.4897 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 107.2035 | 1079.5505 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 80.0296 | 1052.3766
[5 empty] | 416 | 963.901 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 138.4034 | 129.0811 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 138.4034 | 1102.3044 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 129.0811 | 1092.9821 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 113.8861 | 1077.7871 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 86.2456 | 1050.1466
[5 empty] | 418 | 963.258 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 137.6954 | 128.2164 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 137.6954 | 1100.9534 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 128.2164 | 1091.4744 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 112.7657 | 1076.0237 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 84.6586 | 1047.9166
[5 empty] | 420 | 965.836 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 133.7665 | 124.1307 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 133.7665 | 1099.6025 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 124.1307 | 1089.9667 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 108.4244 | 1074.2604 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 79.8506 | 1045.6866
[5 empty] | 422 | 966.309 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 131.9425 | 122.1501 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 131.9425 | 1098.2515 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 122.1501 | 1088.4591 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 106.188 | 1072.497 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 77.1476 | 1043.4566
[5 empty] | 424 | 972.884 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 124.0165 | 114.0674 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 124.0165 | 1096.9005 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 114.0674 | 1086.9514 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 97.8496 | 1070.7336 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 68.3426 | 1041.2266
[5 empty] | 426 | 983.972 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 111.5776 | 101.4717 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 111.5776 | 1095.5496 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 101.4717 | 1085.4437 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 84.9982 | 1068.9702 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.0245 | 1038.9965
[5 empty] | 428 | 994.096 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 100.1026 | 89.8401 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 100.1026 | 1094.1986 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 89.8401 | 1083.9361 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 73.1108 | 1067.2068 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 42.6705 | 1036.7665
[5 empty] | 430 | 991.695 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 101.1527 | 90.7334 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 101.1527 | 1092.8477 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 90.7334 | 1082.4284 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 73.7484 | 1065.4434 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 42.8415 | 1034.5365
[5 empty] | 432 | 984.933 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 106.5637 | 95.9877 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 106.5637 | 1091.4967 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 95.9877 | 1080.9207 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 78.747 | 1063.68 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 47.3735 | 1032.3065
[5 empty] | 434 | 978.185 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 111.9608 | 101.2281 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 111.9608 | 1090.1458 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 101.2281 | 1079.4131 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 83.7316 | 1061.9166 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 51.8915 | 1030.0765
[5 empty] | 436 | 972.686 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 116.1088 | 105.2194 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 116.1088 | 1088.7948 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 105.2194 | 1077.9054 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 87.4672 | 1060.1532 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.1605 | 1027.8465
[5 empty] | 438 | 966.824 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 120.6199 | 109.5737 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 120.6199 | 1087.4439 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 109.5737 | 1076.3977 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 91.5658 | 1058.3898 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 58.7924 | 1025.6164
[5 empty] | 440 | 960.902 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 125.1909 | 113.988 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 125.1909 | 1086.0929 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 113.988 | 1074.89 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 95.7244 | 1056.6264 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 62.4844 | 1023.3864
[5 empty] | 442 | 952.924 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 131.818 | 120.4584 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 131.818 | 1084.742 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 120.4584 | 1073.3824 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 101.939 | 1054.863 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 68.2324 | 1021.1564
[5 empty] | 444 | 945.683 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 137.708 | 126.1917 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 137.708 | 1083.391 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 126.1917 | 1071.8747 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 107.4166 | 1053.0996 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 73.2434 | 1018.9264
[5 empty] | 446 | 941.042 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 140.9981 | 129.325 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 140.9981 | 1082.0401 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 129.325 | 1070.367 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 110.2942 | 1051.3362 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 75.6544 | 1016.6964
[5 empty] | 448 | 937.104 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 143.5851 | 131.7554 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 143.5851 | 1080.6891 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 131.7554 | 1068.8594 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 112.4688 | 1049.5728 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 77.3624 | 1014.4664
[5 empty] | 450 | 939.943 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 139.3951 | 127.4087 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 139.3951 | 1079.3381 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 127.4087 | 1067.3517 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 107.8664 | 1047.8094 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 72.2933 | 1012.2363
[5 empty] | 452 | 944.776 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 133.2112 | 121.068 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 133.2112 | 1077.9872 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 121.068 | 1065.844 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 101.27 | 1046.046 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 65.2303 | 1010.0063
[5 empty] | 454 | 947.762 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 128.8742 | 116.5744 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 128.8742 | 1076.6362 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 116.5744 | 1064.3364 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 96.5206 | 1044.2826 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 60.0143 | 1007.7763
[5 empty] | 456 | 952.649 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 122.6363 | 110.1797 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 122.6363 | 1075.2853 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 110.1797 | 1062.8287 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 89.8702 | 1042.5192 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 52.8973 | 1005.5463
[5 empty] | 458 | 954.554 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 119.3803 | 106.767 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 119.3803 | 1073.9343 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 106.767 | 1061.321 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 86.2018 | 1040.7558 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 48.7623 | 1003.3163
[5 empty] | 460 | 952.37 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 120.2134 | 107.4434 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 120.2134 | 1072.5834 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 107.4434 | 1059.8134 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 86.6224 | 1038.9924 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 48.7163 | 1001.0863
[5 empty] | 462 | 947.552 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 123.6804 | 110.7537 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 123.6804 | 1071.2324 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 110.7537 | 1058.3057 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 89.677 | 1037.229 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 51.3043 | 998.8563
[5 empty] | 464 | 941.898 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 127.9835 | 114.9 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 127.9835 | 1069.8815 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 114.9 | 1056.798 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 93.5676 | 1035.4656 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 54.7282 | 996.6262
[5 empty] | 466 | 940.521 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 128.0095 | 114.7693 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 128.0095 | 1068.5305 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 114.7693 | 1055.2903 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 93.1812 | 1033.7022 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 53.8752 | 994.3962
[5 empty] | 468 | 939.702 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 127.4776 | 114.0807 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 127.4776 | 1067.1796 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 114.0807 | 1053.7827 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 92.2368 | 1031.9388 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 52.4642 | 992.1662
[5 empty] | 470 | 937.147 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 128.6816 | 115.128 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 128.6816 | 1065.8286 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 115.128 | 1052.275 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 93.0284 | 1030.1754 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 52.7892 | 989.9362
[5 empty] | 472 | 933.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 130.6057 | 116.8953 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 130.6057 | 1064.4777 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 116.8953 | 1050.7673 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 94.54 | 1028.412 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 53.8342 | 987.7062
[5 empty] | 474 | 933.184 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 129.9427 | 116.0757 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 129.9427 | 1063.1267 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 116.0757 | 1049.2597 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 93.4646 | 1026.6486 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 52.2922 | 985.4762
[5 empty] | 476 | 939.292 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 122.4838 | 108.46 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 122.4838 | 1061.7758 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 108.46 | 1047.752 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 85.5932 | 1024.8852 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 43.9541 | 983.2461
[5 empty] | 478 | 944.619 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 115.8058 | 101.6253 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 115.8058 | 1060.4248 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 101.6253 | 1046.2443 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 78.5028 | 1023.1218 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 36.3971 | 981.0161
[5 empty] | 480 | 954.023 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 105.0508 | 90.7137 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 105.0508 | 1059.0738 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 90.7137 | 1044.7367 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 67.3354 | 1021.3584 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 24.7631 | 978.7861
[5 empty] | 482 | 968.263 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 89.4599 | 74.966 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 89.4599 | 1057.7229 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 74.966 | 1043.229 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 51.3321 | 1019.5951 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 8.2931 | 976.5561
[5 empty] | 484 | 970.384 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 85.9879 | 71.3373 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 85.9879 | 1056.3719 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 71.3373 | 1041.7213 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 47.4477 | 1017.8317 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 3.9421 | 974.3261
[5 empty] | 486 | 964.636 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 90.385 | 75.5777 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 90.385 | 1055.021 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 75.5777 | 1040.2137 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 51.4323 | 1016.0683 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 7.4601 | 972.0961
[5 empty] | 488 | 956.631 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 97.039 | 82.075 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 97.039 | 1053.67 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 82.075 | 1038.706 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 57.6739 | 1014.3049 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 13.235 | 969.866
[5 empty] | 490 | 947.426 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 104.8931 | 89.7723 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 104.8931 | 1052.3191 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 89.7723 | 1037.1983 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 65.1155 | 1012.5415 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 20.21 | 967.636
[5 empty] | 492 | 941.72 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 109.2481 | 93.9706 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 109.2481 | 1050.9681 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 93.9706 | 1035.6906 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 69.0581 | 1010.7781 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 23.686 | 965.406
[5 empty] | 494 | 935.985 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 113.6322 | 98.198 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 113.6322 | 1049.6172 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 98.198 | 1034.183 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 73.0297 | 1009.0147 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 27.191 | 963.176
[5 empty] | 496 | 930.475 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 117.7912 | 102.2003 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 117.7912 | 1048.2662 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 102.2003 | 1032.6753 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 76.7763 | 1007.2513 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 30.471 | 960.946
[5 empty] | 498 | 927.611 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 119.3043 | 103.5566 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 119.3043 | 1046.9153 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 103.5566 | 1031.1676 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 77.8769 | 1005.4879 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 31.105 | 958.716
[5 empty] | 500 | 931.256 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 114.3083 | 98.404 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 114.3083 | 1045.5643 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 98.404 | 1029.66 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 72.4685 | 1003.7245 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 25.2299 | 956.4859
[5 empty] | 502 | 920.044 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 124.1694 | 108.1083 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 124.1694 | 1044.2134 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 108.1083 | 1028.1523 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 81.9171 | 1001.9611 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 34.2119 | 954.2559
[5 empty] | 504 | 911.78 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 131.0824 | 114.8646 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 131.0824 | 1042.8624 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 114.8646 | 1026.6446 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 88.4177 | 1000.1977 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 40.2459 | 952.0259
[5 empty] | 506 | 907.989 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 133.5224 | 117.148 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 133.5224 | 1041.5114 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 117.148 | 1025.137 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 90.4453 | 998.4343 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 41.8069 | 949.7959
[5 empty] | 508 | 907.289 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 130.7961 | 114.0133 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 130.7961 | 1038.0851 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 114.0133 | 1021.3023 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 86.6419 | 993.9309 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 36.7712 | 944.0602
[5 empty] | 510 | 900.577 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 134.0818 | 116.8906 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 134.0818 | 1034.6588 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 116.8906 | 1017.4676 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 88.8506 | 989.4276 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 37.7476 | 938.3246
[5 empty] | 512 | 902.112 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 129.1205 | 111.5209 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 129.1205 | 1031.2325 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 111.5209 | 1013.6329 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 82.8123 | 984.9243 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 30.4769 | 932.5889
[5 empty] | 514 | 900.179 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 127.6271 | 109.6192 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 127.6271 | 1027.8061 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 109.6192 | 1009.7982 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 80.2419 | 980.4209 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 26.6743 | 926.8533
[5 empty] | 516 | 903.811 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 120.5688 | 102.1525 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 120.5688 | 1024.3798 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 102.1525 | 1005.9635 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 72.1066 | 975.9176 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 17.3066 | 921.1176
[5 empty] | 518 | 910.027 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 110.9265 | 92.1018 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 110.9265 | 1020.9535 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 92.1018 | 1002.1288 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 61.3872 | 971.4142 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 5.3549 | 915.3819
|  |  |  | Reservoir | 520 | 911.131 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 10 | 10 | 10 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 10 | 921.131 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 10 | 921.131 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 10 | 921.131 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 10 | 921.131
[15 empty] | Total Steel Mass (kg): | 298577829.6775