## Summary
Option 5 Summary
Item | Chainage | Value
Pipeline | 0-8 | 1.9 | m - Diameter
Pump Station | 8 | 50 | m - Pumping Head
Pipeline | 8-22 | 1.9 | m - Diameter
Break Pressure | 22 | 10 | m -Elevation
Pipeline | 22-274 | 2.2 | m - Diameter
Break Pressure | 274 | 10 | m - Elevation
Pump Station | 274 | 160 | m - Pumping Head
Pipeline | 274-336 | 2.2 | m -Diameter
Pipeline | 336-508 | 1.8 | m -Diameter
Pipeline | 508-520 | 1.5 | m -Diameter

## Profile data (2)
Longitudinal profile data - Botswana pipeline
| OPTION 1: Pipeline goes through Serule before joining to BPT1 | OPTION2: Pipeline goes directly to BPT1
CHAINAGE (km0 | NGL (m) | NGL (m) |  | Botswana 1
2 | 1069.018 | 1069.018 | Start | Botswana 2
4 | 1067.321 | 1067.321
6 | 1064.035 | 1064.035
8 | 1063.832 | 1063.832
10 | 1067.893 | 1067.893
12 | 1075.133 | 1075.133
14 | 1082.768 | 1082.768
16 | 1089.726 | 1089.726
18 | 1094.131 | 1094.131
20 | 1097.897 | 1097.897
22 | 1101.67 | 1101.67
24 | 1095.952 | 1095.952
26 | 1090.107 | 1090.107
28 | 1085.781 | 1085.781
30 | 1081.89 | 1081.89
32 | 1077.937 | 1077.937
34 | 1074.89 | 1074.89
36 | 1071.114 | 1071.114
38 | 1065.311 | 1065.311
40 | 1059.051 | 1059.051
42 | 1054.28 | 1054.28
44 | 1053.871 | 1053.871
46 | 1050.42 | 1050.42
48 | 1052.704 | 1052.704
50 | 1056.355 | 1056.355
52 | 1058.466 | 1058.466
54 | 1055.99 | 1055.99
56 | 1055.66 | 1055.66
58 | 1056.404 | 1056.404
60 | 1056.841 | 1056.841
62 | 1056.377 | 1056.377
64 | 1052.503 | 1052.503
66 | 1046.022 | 1046.022
68 | 1036.575 | 1036.575
70 | 1031.818 | 1031.818
72 | 1027.675 | 1027.675
74 | 1023.844 | 1023.844
76 | 1020.888 | 1020.888
78 | 1023.648 | 1023.648
80 | 1027.566 | 1027.566
82 | 1032.371 | 1032.371
84 | 1034.983 | 1034.983
86 | 1033.213 | 1033.213
88 | 1031.188 | 1031.188
90 | 1029.08 | 1029.08
92 | 1026.322 | 1026.322
94 | 1023.207 | 1023.207
96 | 1021.503 | 1021.503
98 | 1019.765 | 1019.765
100 | 1018.493 | 1018.493
102 | 1016.444 | 1016.444
104 | 1013.288 | 1013.288
106 | 1007.843 | 1007.843
108 | 1001.282 | 1001.282
110 | 996.609 | 996.609
112 | 992.999 | 992.999
114 | 993.639 | 993.639
116 | 994.611 | 994.611
118 | 995.751 | 995.751
120 | 996.479 | 996.479
122 | 996.147 | 996.147
124 | 992.094 | 992.094
126 | 985.623 | 985.623
128 | 977.759 | 977.759
130 | 969.772 | 969.772
132 | 981.785 | 981.785
134 | 991.458 | 991.458
136 | 987.77 | 987.77
138 | 982.725 | 982.725
140 | 977.559 | 977.559
142 | 975.289 | 975.289
144 | 973.968 | 973.968
146 | 962.473 | 962.473
148 | 951.285 | 951.285
150 | 948.174 | 948.174
152 | 944.641 | 944.641
154 | 941.566 | 941.566
156 | 940.942 | 940.942
158 | 939.726 | 939.726
160 | 936.738 | 936.738
162 | 933.65 | 933.65
164 | 932.745 | 932.745
166 | 931.696 | 931.696
168 | 930.999 | 930.999
170 | 930.885 | 930.885
172 | 930.378 | 930.378
174 | 931.324 | 931.324
176 | 933.53 | 933.53
178 | 932.714 | 932.714
180 | 928.311 | 928.311
182 | 924.179 | 924.179
184 | 928.398 | 928.398
186 | 930.866 | 930.866
188 | 928.411 | 928.411
190 | 927.849 | 927.849
192 | 926.71 | 926.71
194 | 926.201 | 926.201
196 | 924.509 | 924.509
198 | 923.417 | 923.417
200 | 923.011 | 923.011
202 | 921.969 | 921.969
204 | 920.661 | 920.661
206 | 920.243 | 920.243
208 | 919.297 | 919.297
210 | 917.533 | 917.533
212 | 917.684 | 917.684
214 | 915.724 | 915.724
216 | 915.73 | 915.73
218 | 915.584 | 915.584
220 | 915.444 | 915.444
222 | 913.52 | 913.52
224 | 912.524 | 912.524
226 | 912.565 | 912.565
228 | 913.484 | 913.484
230 | 913.545 | 913.545
232 | 914.546 | 914.546
234 | 918.285 | 918.285
236 | 919.357 | 919.357
238 | 918.649 | 918.649
240 | 922.974 | 922.974
242 | 927.375 | 927.375
244 | 929.253 | 929.253
246 | 930.863 | 930.863
248 | 931.924 | 931.924
250 | 936.722 | 936.722
252 | 941.777 | 941.777
254 | 948.143 | 948.143
256 | 955.417 | 955.417
258 | 962.7 | 962.7
260 | 969.281 | 969.281
262 | 980.284 | 980.284
264 | 986.551 | 986.551
266 | 989.198 | 989.198
268 | 994.39 | 994.39
270 | 999.917 | 999.917
272 | 1004.623 | 1004.623
274 | 1008.819 | 1008.819
276 | 1007.834 | 1007.834
278 | 1005.626 | 1005.626
280 | 1001.623 | 1001.623
282 | 1004.052 | 1004.052
284 | 1010.797 | 1010.797
286 | 1014.67 | 1014.67
288 | 1017.319 | 1017.319
290 | 1027.459 | 1027.459
292 | 1031.99 | 1031.99
294 | 1036.254 | 1036.254
296 | 1040.127 | 1040.127
298 | 1044.396 | 1044.396
300 | 1051.339 | 1051.339
302 | 1060.955 | 1060.955
304 | 1070.227 | 1070.227
306 | 1072.691 | 1072.691
308 | 1076.503 | 1076.503
310 | 1083.996 | 1083.996
312 | 1097.188 | 1097.188
314 | 1103.545 | 1103.545
316 | 1105.174 | 1105.174
318 | 1111.657 | 1111.657
320 | 1122.935 | 1122.935
322 | 1128.197 | 1128.197
324 | 1132.561 | 1132.561
326 | 1131.854 | 1131.854
328 | 1133.338 | 1133.338
330 | 1136.405 | 1136.405
332 | 1128.709 | 1128.709
334 | 1120.713 | 1120.713
336 | 1115.226 | 1115.226
338 | 1108.709 | 1108.709
340 | 1102.499 | 1102.499
342 | 1096.349 | 1096.349
344 | 1090.39 | 1090.39
346 | 1087.765 | 1087.765
348 | 1084.661 | 1084.661
350 | 1081.662 | 1081.662
352 | 1076.872 | 1076.872
354 | 1070.898 | 1070.898
356 | 1065.018 | 1065.018
358 | 1059.58 | 1059.58
360 | 1055.284 | 1055.284
362 | 1050.886 | 1050.886
364 | 1052.647 | 1052.647
366 | 1051.117 | 1051.117
368 | 1048.266 | 1048.266
370 | 1040.172 | 1040.172
372 | 1033.483 | 1033.483
374 | 1030.95 | 1030.95
376 | 1032.263 | 1032.263
378 | 1031.391 | 1031.391
380 | 1025.791 | 1025.791
382 | 1020.911 | 1020.911
384 | 1015.65 | 1015.65
386 | 1012.139 | 1012.139
388 | 1010.472 | 1010.472
390 | 1005.401 | 1005.401
392 | 996.666 | 996.666
394 | 991.35 | 991.35
396 | 990.486 | 990.486
398 | 992.761 | 992.761
400 | 999.077 | 999.077
402 | 1001.8 | 1001.8
404 | 1002.224 | 1002.224
406 | 1002.003 | 1002.003
408 | 1003.596 | 1003.596
410 | 994.111 | 994.111
412 | 983.925 | 983.925
414 | 972.347 | 972.347
416 | 963.901 | 963.901
418 | 963.258 | 963.258
420 | 965.836 | 965.872
422 | 966.309 | 966.177
424 | 972.884 | 973.825
426 | 983.972 | 983.972
428 | 994.096 | 994.096
430 | 991.695 | 991.695
432 | 984.933 | 984.933
434 | 978.185 | 974.509
436 | 972.686 | 966.698
438 | 966.824 | 963.618
440 | 960.902 | 957.803
442 | 952.924 | 954.277
444 | 945.683 | 947.182
446 | 941.042 | 938.045
448 | 937.104 | 930.871
450 | 939.943 | 926.391
452 | 944.776 | 918.344
454 | 947.762 | 911.505
456 | 952.649 | 903.61
458 | 954.554 | 900.63
460 | 952.37 | 904.066
462 | 947.552 | 915.092
464 | 941.898 | 905.556
466 | 940.521 | 905.271
468 | 939.702 | 901.918
470 | 937.147 | 895.651
472 | 933.872 | 892.304
474 | 933.184 | 895.279
476 | 939.292 | 896.818
478 | 944.619 | 909.921
480 | 954.023 | 926.295
482 | 968.263 | 924.888
484 | 970.384 | 919.044
486 | 964.636 | 911.164
488 | 956.631 | 903.893
490 | 947.426 | 901.953
492 | 941.72 | 900.198
494 | 935.985 | 904.177
496 | 930.475 | 912.253
498 | 927.611 | 915.297
500 | 931.256 | 919.629
502 | 920.044
504 | 911.78
506 | 907.989
508 | 907.289
510 | 900.577
512 | 902.112
514 | 900.179
516 | 903.811
518 | 910.027
520 | 911.131 |  | End

## Profile data
Longitudinal profile data - Botswana pipeline
| OPTION 1: Pipeline goes through Serule before joining to BPT1 | OPTION2: Pipeline goes directly to BPT1
CHAINAGE (km0 | NGL (m) | NGL (m) |  | Botswana 1
2 | 1069.018 | 1069.018 | Start | Botswana 2
4 | 1067.321 | 1067.321
6 | 1064.035 | 1064.035
8 | 1063.832 | 1063.832
10 | 1067.893 | 1067.893
12 | 1075.133 | 1075.133
14 | 1082.768 | 1082.768
16 | 1089.726 | 1089.726
18 | 1094.131 | 1094.131
20 | 1097.897 | 1097.897
22 | 1101.67 | 1101.67
24 | 1095.952 | 1095.952
26 | 1090.107 | 1090.107
28 | 1085.781 | 1085.781
30 | 1081.89 | 1081.89
32 | 1077.937 | 1077.937
34 | 1074.89 | 1074.89
36 | 1071.114 | 1071.114
38 | 1065.311 | 1065.311
40 | 1059.051 | 1059.051
42 | 1054.28 | 1054.28
44 | 1053.871 | 1053.871
46 | 1050.42 | 1050.42
48 | 1052.704 | 1052.704
50 | 1056.355 | 1056.355
52 | 1058.466 | 1058.466
54 | 1055.99 | 1055.99
56 | 1055.66 | 1055.66
58 | 1056.404 | 1056.404
60 | 1056.841 | 1056.841
62 | 1056.377 | 1056.377
64 | 1052.503 | 1052.503
66 | 1046.022 | 1046.022
68 | 1036.575 | 1036.575
70 | 1031.818 | 1031.818
72 | 1027.675 | 1027.675
74 | 1023.844 | 1023.844
76 | 1020.888 | 1020.888
78 | 1023.648 | 1023.648
80 | 1027.566 | 1027.566
82 | 1032.371 | 1032.371
84 | 1034.983 | 1034.983
86 | 1033.213 | 1033.213
88 | 1031.188 | 1031.188
90 | 1029.08 | 1029.08
92 | 1026.322 | 1026.322
94 | 1023.207 | 1023.207
96 | 1021.503 | 1021.503
98 | 1019.765 | 1019.765
100 | 1018.493 | 1018.493
102 | 1016.444 | 1016.444
104 | 1013.288 | 1013.288
106 | 1007.843 | 1007.843
108 | 1001.282 | 1001.282
110 | 996.609 | 996.609
112 | 992.999 | 992.999
114 | 993.639 | 993.639
116 | 994.611 | 994.611
118 | 995.751 | 995.751
120 | 996.479 | 996.479
122 | 996.147 | 996.147
124 | 992.094 | 992.094
126 | 985.623 | 985.623
128 | 977.759 | 977.759
130 | 969.772 | 969.772
132 | 981.785 | 981.785
134 | 991.458 | 991.458
136 | 987.77 | 987.77
138 | 982.725 | 982.725
140 | 977.559 | 977.559
142 | 975.289 | 975.289
144 | 973.968 | 973.968
146 | 962.473 | 962.473
148 | 951.285 | 951.285
150 | 948.174 | 948.174
152 | 944.641 | 944.641
154 | 941.566 | 941.566
156 | 940.942 | 940.942
158 | 939.726 | 939.726
160 | 936.738 | 936.738
162 | 933.65 | 933.65
164 | 932.745 | 932.745
166 | 931.696 | 931.696
168 | 930.999 | 930.999
170 | 930.885 | 930.885
172 | 930.378 | 930.378
174 | 931.324 | 931.324
176 | 933.53 | 933.53
178 | 932.714 | 932.714
180 | 928.311 | 928.311
182 | 924.179 | 924.179
184 | 928.398 | 928.398
186 | 930.866 | 930.866
188 | 928.411 | 928.411
190 | 927.849 | 927.849
192 | 926.71 | 926.71
194 | 926.201 | 926.201
196 | 924.509 | 924.509
198 | 923.417 | 923.417
200 | 923.011 | 923.011
202 | 921.969 | 921.969
204 | 920.661 | 920.661
206 | 920.243 | 920.243
208 | 919.297 | 919.297
210 | 917.533 | 917.533
212 | 917.684 | 917.684
214 | 915.724 | 915.724
216 | 915.73 | 915.73
218 | 915.584 | 915.584
220 | 915.444 | 915.444
222 | 913.52 | 913.52
224 | 912.524 | 912.524
226 | 912.565 | 912.565
228 | 913.484 | 913.484
230 | 913.545 | 913.545
232 | 914.546 | 914.546
234 | 918.285 | 918.285
236 | 919.357 | 919.357
238 | 918.649 | 918.649
240 | 922.974 | 922.974
242 | 927.375 | 927.375
244 | 929.253 | 929.253
246 | 930.863 | 930.863
248 | 931.924 | 931.924
250 | 936.722 | 936.722
252 | 941.777 | 941.777
254 | 948.143 | 948.143
256 | 955.417 | 955.417
258 | 962.7 | 962.7
260 | 969.281 | 969.281
262 | 980.284 | 980.284
264 | 986.551 | 986.551
266 | 989.198 | 989.198
268 | 994.39 | 994.39
270 | 999.917 | 999.917
272 | 1004.623 | 1004.623
274 | 1008.819 | 1008.819
276 | 1007.834 | 1007.834
278 | 1005.626 | 1005.626
280 | 1001.623 | 1001.623
282 | 1004.052 | 1004.052
284 | 1010.797 | 1010.797
286 | 1014.67 | 1014.67
288 | 1017.319 | 1017.319
290 | 1027.459 | 1027.459
292 | 1031.99 | 1031.99
294 | 1036.254 | 1036.254
296 | 1040.127 | 1040.127
298 | 1044.396 | 1044.396
300 | 1051.339 | 1051.339
302 | 1060.955 | 1060.955
304 | 1070.227 | 1070.227
306 | 1072.691 | 1072.691
308 | 1076.503 | 1076.503
310 | 1083.996 | 1083.996
312 | 1097.188 | 1097.188
314 | 1103.545 | 1103.545
316 | 1105.174 | 1105.174
318 | 1111.657 | 1111.657
320 | 1122.935 | 1122.935
322 | 1128.197 | 1128.197
324 | 1132.561 | 1132.561
326 | 1131.854 | 1131.854
328 | 1133.338 | 1133.338
330 | 1136.405 | 1136.405
332 | 1128.709 | 1128.709
334 | 1120.713 | 1120.713
336 | 1115.226 | 1115.226
338 | 1108.709 | 1108.709
340 | 1102.499 | 1102.499
342 | 1096.349 | 1096.349
344 | 1090.39 | 1090.39
346 | 1087.765 | 1087.765
348 | 1084.661 | 1084.661
350 | 1081.662 | 1081.662
352 | 1076.872 | 1076.872
354 | 1070.898 | 1070.898
356 | 1065.018 | 1065.018
358 | 1059.58 | 1059.58
360 | 1055.284 | 1055.284
362 | 1050.886 | 1050.886
364 | 1052.647 | 1052.647
366 | 1051.117 | 1051.117
368 | 1048.266 | 1048.266
370 | 1040.172 | 1040.172
372 | 1033.483 | 1033.483
374 | 1030.95 | 1030.95
376 | 1032.263 | 1032.263
378 | 1031.391 | 1031.391
380 | 1025.791 | 1025.791
382 | 1020.911 | 1020.911
384 | 1015.65 | 1015.65
386 | 1012.139 | 1012.139
388 | 1010.472 | 1010.472
390 | 1005.401 | 1005.401
392 | 996.666 | 996.666
394 | 991.35 | 991.35
396 | 990.486 | 990.486
398 | 992.761 | 992.761
400 | 999.077 | 999.077
402 | 1001.8 | 1001.8
404 | 1002.224 | 1002.224
406 | 1002.003 | 1002.003
408 | 1003.596 | 1003.596
410 | 994.111 | 994.111
412 | 983.925 | 983.925
414 | 972.347 | 972.347
416 | 963.901 | 963.901
418 | 963.258 | 963.258
420 | 965.836 | 965.872
422 | 966.309 | 966.177
424 | 972.884 | 973.825
426 | 983.972 | 983.972
428 | 994.096 | 994.096
430 | 991.695 | 991.695
432 | 984.933 | 984.933
434 | 978.185 | 974.509
436 | 972.686 | 966.698
438 | 966.824 | 963.618
440 | 960.902 | 957.803
442 | 952.924 | 954.277
444 | 945.683 | 947.182
446 | 941.042 | 938.045
448 | 937.104 | 930.871
450 | 939.943 | 926.391
452 | 944.776 | 918.344
454 | 947.762 | 911.505
456 | 952.649 | 903.61
458 | 954.554 | 900.63
460 | 952.37 | 904.066
462 | 947.552 | 915.092
464 | 941.898 | 905.556
466 | 940.521 | 905.271
468 | 939.702 | 901.918
470 | 937.147 | 895.651
472 | 933.872 | 892.304
474 | 933.184 | 895.279
476 | 939.292 | 896.818
478 | 944.619 | 909.921
480 | 954.023 | 926.295
482 | 968.263 | 924.888
484 | 970.384 | 919.044
486 | 964.636 | 911.164
488 | 956.631 | 903.893
490 | 947.426 | 901.953
492 | 941.72 | 900.198
494 | 935.985 | 904.177
496 | 930.475 | 912.253
498 | 927.611 | 915.297
500 | 931.256 | 919.629
502 | 920.044
504 | 911.78
506 | 907.989
508 | 907.289
510 | 900.577
512 | 902.112
514 | 900.179
516 | 903.811
518 | 910.027
520 | 911.131 |  | End

## Flow Rate Calculations
Estimated Transfer Rate Demand | 100 | Mm3/a
Availible Days | 365
Pumping Hours | 24
Pf | 1.052
Pl | 1.02
PR | 1.2
Peak Design Flow | 4.0831 | m3/s

## Calculation Constants
Friction Factors
Ks (mm) - New | 0.03
Ks (mm) - Average | 0.06
Ks (mm) - Old | 0.15
Ks (mm) - Biofilm | 0.5
Kinemeatic Viscosity | 1.13e-06 | m2/s
Minor Loss - k | 150
Grade of Steel | X42
Yeild Capacity | 300 | Mpa
Design % of Yeild | 50%
Minimum D/t ratio | 160 | mm/mm

## Hydraulics
Option 3A |  |  |  | Option 3A | [12 empty] | Option 3A
Pump Station |  |  |  | Pipe Line | [9 empty] | Steel Pipeline Design |  |  | New Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Average Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Old Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Biofilm Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes
Name | Chainage (km) | Elevation (m) | Pumped Head (m) | Reference | Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Flow Rate (m3/s) | PipeVelocity (m/s) | Re | Static Head (m) | Dynamic Head (m) | Design Pressure (m) | Pipe Wall thickness (mm) | Steel Mass (kg) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m)
PS 1 | 8 | 1063.832 | 50 | Reservoir | 2 | 1069.018 | 0 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 10 | 10 | 10 | 11.875 | 0 | 0.00867 |  |  | 0 | 0 | 10 | 1079.018 | 0.0097304 |  |  | 0 | 0 | 10 | 1079.018 | 0.011459 |  |  | 0 | 0 | 10 | 1079.018 | 0.014543 |  |  | 0 | 0 | 10 | 1079.018
PS 2 | 274 | 1008.819 | 160 |  | 4 | 1067.321 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 11.697 | 10.6713 | 11.697 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 10.6713 | 1077.9923 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 10.5534 | 1077.8744 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 10.361 | 1077.682 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 10.011 | 1077.332
[5 empty] | 6 | 1064.035 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 14.983 | 12.9317 | 14.983 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 12.9317 | 1076.9667 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 12.6957 | 1076.7307 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 12.311 | 1076.346 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 11.6111 | 1075.6461
|  |  |  | Pump Station | 8 | 1063.832 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 62.109 | 61.7551 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 50 | 62.109 | 1125.941 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 50 | 61.7551 | 1125.5871 | 0.011459 | 1.275 | 0.060983 | 1.336 | 50 | 61.1781 | 1125.0101 | 0.014543 | 1.625 | 0.060983 | 1.686 | 50 | 60.1281 | 1123.9601
[5 empty] | 10 | 1067.893 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 57.0224 | 56.5504 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 57.0224 | 1124.9154 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 56.5504 | 1124.4434 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 55.7811 | 1123.6741 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 54.3812 | 1122.2742
Reservoirs |  |  |  |  | 12 | 1075.133 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 48.7567 | 48.1668 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 48.7567 | 1123.8897 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 48.1668 | 1123.2998 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 47.2051 | 1122.3381 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 45.4552 | 1120.5882
Name | Chainage (km) | Water Elevation (m) | Height |  | 14 | 1082.768 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 40.096 | 39.3881 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 40.096 | 1122.864 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 39.3881 | 1122.1561 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 38.2341 | 1121.0021 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 36.1343 | 1118.9023
Supply Resrvoir | 2 | 1079.018 | 10 |  | 16 | 1089.726 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 32.1124 | 31.2865 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 32.1124 | 1121.8384 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 31.2865 | 1121.0125 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 29.9401 | 1119.6661 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.4903 | 1117.2163
BPT 3 | 22 | 1111.67 | 10 |  | 18 | 1094.131 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 26.6817 | 25.7378 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 26.6817 | 1120.8127 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 25.7378 | 1119.8688 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 24.1991 | 1118.3301 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 21.3994 | 1115.5304
BPT 4 | 274 | 1018.819 | 10 |  | 20 | 1097.897 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 21.8901 | 20.8282 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 21.8901 | 1119.7871 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 20.8282 | 1118.7252 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 19.0972 | 1116.9942 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 15.9474 | 1113.8444
BPT 1 | 520 | 921.131 | 10 | Reservoir | 22 | 1101.67 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 10 | 10 | 10 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 10 | 1111.67 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 10 | 1111.67 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 10 | 1111.67 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 10 | 1111.67 | 1112.0975
[5 empty] | 24 | 1095.952 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 15.718 | 15.2314 | 15.718 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 15.2314 | 1111.1834 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 15.1767 | 1111.1287 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 15.0879 | 1111.0399 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 14.9273 | 1110.8793 | -0.42746
[5 empty] | 26 | 1090.107 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 21.563 | 20.5898 | 21.563 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 20.5898 | 1110.6968 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 20.4805 | 1110.5875 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 20.3027 | 1110.4097 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 19.9816 | 1110.0886
[5 empty] | 28 | 1085.781 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 25.889 | 24.4292 | 25.889 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 24.4292 | 1110.2102 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 24.2652 | 1110.0462 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 23.9986 | 1109.7796 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 23.5169 | 1109.2979
|  | 92.851 |  |  | 30 | 1081.89 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 29.78 | 27.8335 | 29.78 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 27.8335 | 1109.7235 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 27.6149 | 1109.5049 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 27.2594 | 1109.1494 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 26.6172 | 1108.5072
[5 empty] | 32 | 1077.937 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 33.733 | 31.2999 | 33.733 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 31.2999 | 1109.2369 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 31.0266 | 1108.9636 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 30.5823 | 1108.5193 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 29.7795 | 1107.7165
[5 empty] | 34 | 1074.89 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 36.78 | 33.8603 | 36.78 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 33.8603 | 1108.7503 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 33.5324 | 1108.4224 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 32.9991 | 1107.8891 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 32.0358 | 1106.9258
[5 empty] | 36 | 1071.114 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 40.556 | 37.1497 | 40.556 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 37.1497 | 1108.2637 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 36.7671 | 1107.8811 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 36.145 | 1107.259 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 35.0212 | 1106.1352
Route | Botswana 1 |  |  |  | 38 | 1065.311 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 46.359 | 42.4661 | 46.359 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 42.4661 | 1107.7771 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 42.0288 | 1107.3398 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 41.3179 | 1106.6289 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 40.0335 | 1105.3445
Option | 3A |  |  |  | 40 | 1059.051 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 52.619 | 48.2395 | 52.619 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 48.2395 | 1107.2905 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 47.7475 | 1106.7985 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 46.9477 | 1105.9987 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 45.5028 | 1104.5538
[5 empty] | 42 | 1054.28 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 57.39 | 52.5239 | 57.39 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 52.5239 | 1106.8039 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 51.9773 | 1106.2573 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 51.0886 | 1105.3686 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 49.4831 | 1103.7631
[5 empty] | 44 | 1053.871 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 57.799 | 52.4462 | 57.799 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 52.4462 | 1106.3172 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 51.845 | 1105.716 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 50.8674 | 1104.7384 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 49.1014 | 1102.9724
[5 empty] | 46 | 1050.42 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 61.25 | 55.4106 | 61.25 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 55.4106 | 1105.8306 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 54.7547 | 1105.1747 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 53.6883 | 1104.1083 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 51.7617 | 1102.1817
[5 empty] | 48 | 1052.704 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 58.966 | 52.64 | 58.966 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 52.64 | 1105.344 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 51.9294 | 1104.6334 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 50.7741 | 1103.4781 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 48.687 | 1101.391
[5 empty] | 50 | 1056.355 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 55.315 | 48.5024 | 55.315 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 48.5024 | 1104.8574 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 47.7372 | 1104.0922 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 46.493 | 1102.848 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 44.2453 | 1100.6003
[5 empty] | 52 | 1058.466 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 53.204 | 45.9048 | 53.204 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 45.9048 | 1104.3708 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 45.0849 | 1103.5509 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 43.7519 | 1102.2179 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 41.3436 | 1099.8096
[5 empty] | 54 | 1055.99 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 55.68 | 47.8942 | 55.68 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 47.8942 | 1103.8842 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 47.0196 | 1103.0096 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 45.5977 | 1101.5877 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 43.0289 | 1099.0189
[5 empty] | 56 | 1055.66 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 56.01 | 47.7376 | 56.01 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 47.7376 | 1103.3976 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 46.8084 | 1102.4684 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 45.2976 | 1100.9576 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 42.5682 | 1098.2282
[5 empty] | 58 | 1056.404 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 55.266 | 46.507 | 55.266 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 46.507 | 1102.911 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 45.5231 | 1101.9271 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 43.9234 | 1100.3274 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 41.0335 | 1097.4375
[5 empty] | 60 | 1056.841 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 54.829 | 45.5833 | 54.829 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 45.5833 | 1102.4243 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 44.5448 | 1101.3858 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 42.8563 | 1099.6973 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 39.8058 | 1096.6468
[5 empty] | 62 | 1056.377 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 55.293 | 45.5607 | 55.293 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 45.5607 | 1101.9377 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 44.4675 | 1100.8445 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 42.6901 | 1099.0671 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 39.4792 | 1095.8562
[5 empty] | 64 | 1052.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 59.167 | 48.9481 | 59.167 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 48.9481 | 1101.4511 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 47.8003 | 1100.3033 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 45.934 | 1098.437 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 42.5625 | 1095.0655
[5 empty] | 66 | 1046.022 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 65.648 | 54.9425 | 65.648 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 54.9425 | 1100.9645 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 53.74 | 1099.762 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 51.7849 | 1097.8069 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 48.2528 | 1094.2748
[5 empty] | 68 | 1036.575 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 75.095 | 63.9029 | 75.095 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 63.9029 | 1100.4779 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 62.6457 | 1099.2207 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 60.6017 | 1097.1767 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 56.9091 | 1093.4841
[5 empty] | 70 | 1031.818 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 79.852 | 68.1733 | 79.852 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 68.1733 | 1099.9913 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 66.8614 | 1098.6794 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 64.7286 | 1096.5466 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 60.8754 | 1092.6934
[5 empty] | 72 | 1027.675 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 83.995 | 71.8297 | 83.995 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 71.8297 | 1099.5047 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 70.4632 | 1098.1382 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 68.2414 | 1095.9164 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 64.2277 | 1091.9027
[5 empty] | 74 | 1023.844 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 87.826 | 75.174 | 87.826 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 75.174 | 1099.018 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 73.7529 | 1097.5969 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 71.4423 | 1095.2863 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 67.268 | 1091.112
[5 empty] | 76 | 1020.888 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 90.782 | 77.6434 | 90.782 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 77.6434 | 1098.5314 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 76.1676 | 1097.0556 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 73.7681 | 1094.6561 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 69.4333 | 1090.3213
[5 empty] | 78 | 1023.648 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 88.022 | 74.3968 | 88.022 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 74.3968 | 1098.0448 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 72.8663 | 1096.5143 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 70.378 | 1094.026 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 65.8826 | 1089.5306
[5 empty] | 80 | 1027.566 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 84.104 | 69.9922 | 84.104 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 69.9922 | 1097.5582 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 68.4071 | 1095.9731 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 65.8298 | 1093.3958 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 61.1739 | 1088.7399
[5 empty] | 82 | 1032.371 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 79.299 | 64.7006 | 79.299 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 64.7006 | 1097.0716 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 63.0608 | 1095.4318 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 60.3947 | 1092.7657 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 55.5782 | 1087.9492
[5 empty] | 84 | 1034.983 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 76.687 | 61.602 | 76.687 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 61.602 | 1096.585 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 59.9075 | 1094.8905 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 57.1526 | 1092.1356 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 52.1755 | 1087.1585
[5 empty] | 86 | 1033.213 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 78.457 | 62.8854 | 78.457 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 62.8854 | 1096.0984 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 61.1363 | 1094.3493 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 58.2924 | 1091.5054 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 53.1548 | 1086.3678
[5 empty] | 88 | 1031.188 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 80.482 | 64.4237 | 80.482 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 64.4237 | 1095.6117 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 62.62 | 1093.808 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 59.6873 | 1090.8753 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 54.3892 | 1085.5772
[5 empty] | 90 | 1029.08 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 82.59 | 66.0451 | 82.59 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 66.0451 | 1095.1251 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 64.1867 | 1093.2667 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 61.1651 | 1090.2451 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 55.7065 | 1084.7865
[5 empty] | 92 | 1026.322 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 85.348 | 68.3165 | 85.348 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 68.3165 | 1094.6385 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 66.4034 | 1092.7254 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 63.293 | 1089.615 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 57.6738 | 1083.9958
[5 empty] | 94 | 1023.207 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 88.463 | 70.9449 | 88.463 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 70.9449 | 1094.1519 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 68.9772 | 1092.1842 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 65.7778 | 1088.9848 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 59.9981 | 1083.2051
[5 empty] | 96 | 1021.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 90.167 | 72.1623 | 90.167 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 72.1623 | 1093.6653 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 70.1399 | 1091.6429 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 66.8517 | 1088.3547 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 60.9114 | 1082.4144
[5 empty] | 98 | 1019.765 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 91.905 | 73.4137 | 91.905 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 73.4137 | 1093.1787 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 71.3366 | 1091.1016 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 67.9596 | 1087.7246 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 61.8587 | 1081.6237
[5 empty] | 100 | 1018.493 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 93.177 | 74.1991 | 93.177 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 74.1991 | 1092.6921 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 72.0673 | 1090.5603 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 68.6014 | 1087.0944 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 62.34 | 1080.833
[5 empty] | 102 | 1016.444 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 95.226 | 75.7614 | 95.226 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 75.7614 | 1092.2054 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 73.5751 | 1090.0191 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 70.0203 | 1086.4643 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 63.5983 | 1080.0423
[5 empty] | 104 | 1013.288 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 98.382 | 78.4308 | 98.382 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 78.4308 | 1091.7188 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 76.1898 | 1089.4778 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 72.5461 | 1085.8341 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 65.9636 | 1079.2516
[5 empty] | 106 | 1007.843 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 103.827 | 83.3892 | 103.827 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 83.3892 | 1091.2322 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 81.0935 | 1088.9365 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 77.361 | 1085.204 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 70.6179 | 1078.4609
[5 empty] | 108 | 1001.282 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 110.388 | 89.4636 | 110.388 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 89.4636 | 1090.7456 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 87.1132 | 1088.3952 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 83.2918 | 1084.5738 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 76.3882 | 1077.6702
[5 empty] | 110 | 996.609 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 115.061 | 93.65 | 115.061 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 93.65 | 1090.259 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 91.245 | 1087.854 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 87.3347 | 1083.9437 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 80.2705 | 1076.8795
[5 empty] | 112 | 992.999 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 118.671 | 96.7734 | 118.671 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 96.7734 | 1089.7724 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 94.3137 | 1087.3127 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 90.3146 | 1083.3136 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 83.0898 | 1076.0888
[5 empty] | 114 | 993.639 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 118.031 | 95.6468 | 118.031 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 95.6468 | 1089.2858 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 93.1324 | 1086.7714 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 89.0444 | 1082.6834 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 81.6592 | 1075.2982
[5 empty] | 116 | 994.611 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 117.059 | 94.1881 | 117.059 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 94.1881 | 1088.7991 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 91.6192 | 1086.2302 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 87.4423 | 1082.0533 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 79.8965 | 1074.5075
[5 empty] | 118 | 995.751 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 115.919 | 92.5615 | 115.919 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 92.5615 | 1088.3125 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 89.9379 | 1085.6889 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 85.6721 | 1081.4231 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 77.9658 | 1073.7168
[5 empty] | 120 | 996.479 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 115.191 | 91.3469 | 115.191 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 91.3469 | 1087.8259 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 88.6686 | 1085.1476 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 84.314 | 1080.793 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 76.4471 | 1072.9261
[5 empty] | 122 | 996.147 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 115.523 | 91.1923 | 115.523 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 91.1923 | 1087.3393 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 88.4593 | 1084.6063 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 84.0158 | 1080.1628 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 75.9884 | 1072.1354
[5 empty] | 124 | 992.094 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 119.576 | 94.7587 | 119.576 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 94.7587 | 1086.8527 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 91.9711 | 1084.0651 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 87.4387 | 1079.5327 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 79.2507 | 1071.3447
[5 empty] | 126 | 985.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 126.047 | 100.7431 | 126.047 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 100.7431 | 1086.3661 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 97.9008 | 1083.5238 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 93.2796 | 1078.9026 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 84.931 | 1070.554
[5 empty] | 128 | 977.759 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 133.911 | 108.1205 | 133.911 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 108.1205 | 1085.8795 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 105.2235 | 1082.9825 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 100.5134 | 1078.2724 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 92.0043 | 1069.7633
[5 empty] | 130 | 969.772 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 141.898 | 115.6209 | 141.898 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 115.6209 | 1085.3929 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 112.6692 | 1082.4412 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 107.8703 | 1077.6423 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 99.2006 | 1068.9726
[5 empty] | 132 | 981.785 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 129.885 | 103.1212 | 129.885 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 103.1212 | 1084.9062 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 100.115 | 1081.9 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 95.2271 | 1077.0121 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 86.3969 | 1068.1819
[5 empty] | 134 | 991.458 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 120.212 | 92.9616 | 120.212 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 92.9616 | 1084.4196 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 89.9007 | 1081.3587 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 84.924 | 1076.382 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 75.9332 | 1067.3912
[5 empty] | 136 | 987.77 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 123.9 | 96.163 | 123.9 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 96.163 | 1083.933 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 93.0474 | 1080.8174 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 87.9818 | 1075.7518 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 78.8305 | 1066.6005
[5 empty] | 138 | 982.725 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 128.945 | 100.7214 | 128.945 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 100.7214 | 1083.4464 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 97.5511 | 1080.2761 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 92.3967 | 1075.1217 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 83.0848 | 1065.8098
[5 empty] | 140 | 977.559 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 134.111 | 105.4008 | 134.111 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 105.4008 | 1082.9598 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 102.1759 | 1079.7349 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 96.9326 | 1074.4916 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 87.4602 | 1065.0192
[5 empty] | 142 | 975.289 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 136.381 | 107.1842 | 136.381 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 107.1842 | 1082.4732 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 103.9046 | 1079.1936 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 98.5724 | 1073.8614 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 88.9395 | 1064.2285
[5 empty] | 144 | 973.968 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 137.702 | 108.0186 | 137.702 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 108.0186 | 1081.9866 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 104.6843 | 1078.6523 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 99.2633 | 1073.2313 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 89.4698 | 1063.4378
[5 empty] | 146 | 962.473 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 149.197 | 119.0269 | 149.197 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 119.0269 | 1081.4999 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 115.6381 | 1078.1111 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 110.1281 | 1072.6011 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 100.1741 | 1062.6471
[5 empty] | 148 | 951.285 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 160.385 | 129.7283 | 160.385 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 129.7283 | 1081.0133 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 126.2848 | 1077.5698 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 120.686 | 1071.971 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 110.5714 | 1061.8564
[5 empty] | 150 | 948.174 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 163.496 | 132.3527 | 163.496 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 132.3527 | 1080.5267 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 128.8545 | 1077.0285 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 123.1668 | 1071.3408 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 112.8917 | 1061.0657
[5 empty] | 152 | 944.641 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 167.029 | 135.3991 | 167.029 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 135.3991 | 1080.0401 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 131.8462 | 1076.4872 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 126.0697 | 1070.7107 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 115.634 | 1060.275
[5 empty] | 154 | 941.566 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 170.104 | 137.9875 | 170.104 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 137.9875 | 1079.5535 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 134.38 | 1075.946 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 128.5146 | 1070.0806 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 117.9183 | 1059.4843
[5 empty] | 156 | 940.942 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 170.728 | 138.1249 | 170.728 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 138.1249 | 1079.0669 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 134.4627 | 1075.4047 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 128.5084 | 1069.4504 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 117.7516 | 1058.6936
[5 empty] | 158 | 939.726 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 171.944 | 138.8543 | 171.944 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 138.8543 | 1078.5803 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 135.1374 | 1074.8634 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 129.0943 | 1068.8203 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 118.1769 | 1057.9029
[5 empty] | 160 | 936.738 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 174.932 | 141.3556 | 174.932 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 141.3556 | 1078.0936 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 137.5841 | 1074.3221 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 131.4521 | 1068.1901 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 120.3742 | 1057.1122
[5 empty] | 162 | 933.65 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 178.02 | 143.957 | 178.02 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 143.957 | 1077.607 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 140.1309 | 1073.7809 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 133.91 | 1067.56 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 122.6715 | 1056.3215
[5 empty] | 164 | 932.745 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 178.925 | 144.3754 | 178.925 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 144.3754 | 1077.1204 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 140.4946 | 1073.2396 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 134.1848 | 1066.9298 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 122.7858 | 1055.5308
[5 empty] | 166 | 931.696 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 179.974 | 144.9378 | 179.974 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 144.9378 | 1076.6338 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 141.0023 | 1072.6983 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 134.6037 | 1066.2997 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 123.0441 | 1054.7401
[5 empty] | 168 | 930.999 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 180.671 | 145.1482 | 180.671 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 145.1482 | 1076.1472 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 141.158 | 1072.157 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 134.6706 | 1065.6696 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 122.9505 | 1053.9495
[5 empty] | 170 | 930.885 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 180.785 | 144.7756 | 180.785 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 144.7756 | 1075.6606 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 140.7308 | 1071.6158 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 134.1544 | 1065.0394 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 122.2738 | 1053.1588
[5 empty] | 172 | 930.378 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 181.292 | 144.796 | 181.292 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 144.796 | 1075.174 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 140.6965 | 1071.0745 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 134.0313 | 1064.4093 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 121.9901 | 1052.3681
[5 empty] | 174 | 931.324 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 180.346 | 143.3633 | 180.346 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 143.3633 | 1074.6873 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 139.2092 | 1070.5332 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 132.4551 | 1063.7791 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 120.2534 | 1051.5774
[5 empty] | 176 | 933.53 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 178.14 | 140.6707 | 178.14 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 140.6707 | 1074.2007 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 136.462 | 1069.992 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 129.619 | 1063.149 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 117.2567 | 1050.7867
[5 empty] | 178 | 932.714 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 178.956 | 141.0001 | 178.956 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 141.0001 | 1073.7141 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 136.7367 | 1069.4507 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 129.8048 | 1062.5188 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 117.282 | 1049.996
[5 empty] | 180 | 928.311 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 183.359 | 144.9165 | 183.359 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 144.9165 | 1073.2275 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 140.5984 | 1068.9094 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 133.5777 | 1061.8887 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 120.8943 | 1049.2053
[5 empty] | 182 | 924.179 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 187.491 | 148.5619 | 187.491 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 148.5619 | 1072.7409 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 144.1891 | 1068.3681 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 137.0796 | 1061.2586 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 124.2356 | 1048.4146
[5 empty] | 184 | 928.398 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 183.272 | 143.8563 | 183.272 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 143.8563 | 1072.2543 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 139.4289 | 1067.8269 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 132.2304 | 1060.6284 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 119.2259 | 1047.6239
[5 empty] | 186 | 930.866 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 180.804 | 140.9017 | 180.804 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 140.9017 | 1071.7677 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 136.4196 | 1067.2856 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 129.1323 | 1059.9983 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 115.9672 | 1046.8332
[5 empty] | 188 | 928.411 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 183.259 | 142.87 | 183.259 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 142.87 | 1071.281 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 138.3333 | 1066.7443 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 130.9571 | 1059.3681 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 117.6315 | 1046.0425
[5 empty] | 190 | 927.849 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 183.821 | 142.9454 | 183.821 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 142.9454 | 1070.7944 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 138.354 | 1066.203 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 130.889 | 1058.738 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 117.4028 | 1045.2518
[5 empty] | 192 | 926.71 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 184.96 | 143.5978 | 184.96 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 143.5978 | 1070.3078 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 138.9518 | 1065.6618 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 131.3978 | 1058.1078 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 117.7511 | 1044.4611
[5 empty] | 194 | 926.201 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 185.469 | 143.6202 | 185.469 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 143.6202 | 1069.8212 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 138.9195 | 1065.1205 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 131.2767 | 1057.4777 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 117.4695 | 1043.6705
[5 empty] | 196 | 924.509 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 187.161 | 144.8256 | 187.161 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 144.8256 | 1069.3346 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 140.0702 | 1064.5792 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 132.3385 | 1056.8475 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 118.3708 | 1042.8798
[5 empty] | 198 | 923.417 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 188.253 | 145.431 | 188.253 | 13.8052 | 1488612.6665 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 145.431 | 1068.848 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 140.6209 | 1064.0379 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 132.8004 | 1056.2174 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 118.6721 | 1042.0891
[5 empty] | 200 | 923.011 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 188.659 | 145.3504 | 188.659 | 13.835 | 1491802.7991 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 145.3504 | 1068.3614 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 140.4857 | 1063.4967 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 132.5763 | 1055.5873 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 118.2874 | 1041.2984
[5 empty] | 202 | 921.969 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 189.701 | 145.9058 | 189.701 | 13.9114 | 1499989.8822 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 145.9058 | 1067.8748 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 140.9864 | 1062.9554 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 132.9881 | 1054.9571 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 118.5387 | 1040.5077
[5 empty] | 204 | 920.661 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 191.009 | 146.7271 | 191.009 | 14.0073 | 1510266.1346 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 146.7271 | 1067.3881 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 141.7531 | 1062.4141 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 133.666 | 1054.327 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 119.056 | 1039.717
[5 empty] | 206 | 920.243 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 191.427 | 146.6585 | 191.427 | 14.038 | 1513549.9444 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 146.6585 | 1066.9015 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 141.6299 | 1061.8729 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 133.4538 | 1053.6968 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 118.6833 | 1038.9263
[5 empty] | 208 | 919.297 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 192.373 | 147.1179 | 192.373 | 14.1074 | 1520981.3822 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 147.1179 | 1066.4149 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 142.0346 | 1061.3316 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 133.7697 | 1053.0667 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 118.8386 | 1038.1356
[5 empty] | 210 | 917.533 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 194.137 | 148.3953 | 194.137 | 14.2367 | 1534837.4676 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 148.3953 | 1065.9283 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 143.2573 | 1060.7903 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 134.9035 | 1052.4365 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 119.8119 | 1037.3449
[5 empty] | 212 | 917.684 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 193.986 | 147.7577 | 193.986 | 14.2256 | 1533651.4388 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 147.7577 | 1065.4417 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 142.565 | 1060.249 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 134.1224 | 1051.8064 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 118.8702 | 1036.5542
[5 empty] | 214 | 915.724 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 195.946 | 149.2311 | 195.946 | 14.3694 | 1549045.3101 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 149.2311 | 1064.9551 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 143.9838 | 1059.7078 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 135.4523 | 1051.1763 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 120.0395 | 1035.7635
[5 empty] | 216 | 915.73 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 195.94 | 148.7385 | 195.94 | 14.3689 | 1548998.1891 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 148.7385 | 1064.4685 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 143.4365 | 1059.1665 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 134.8161 | 1050.5461 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 119.2428 | 1034.9728
[5 empty] | 218 | 915.584 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 196.086 | 148.3978 | 196.086 | 14.3796 | 1550144.7944 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 148.3978 | 1063.9818 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 143.0412 | 1058.6252 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 134.332 | 1049.916 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 118.5981 | 1034.1821
[5 empty] | 220 | 915.444 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 196.226 | 148.0512 | 196.226 | 14.3899 | 1551244.2682 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 148.0512 | 1063.4952 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 142.6399 | 1058.0839 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 133.8418 | 1049.2858 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 117.9475 | 1033.3915
[5 empty] | 222 | 913.52 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 198.15 | 149.4886 | 198.15 | 14.531 | 1566353.1271 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 149.4886 | 1063.0086 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 144.0227 | 1057.5427 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 135.1357 | 1048.6557 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 119.0808 | 1032.6008
[5 empty] | 224 | 912.524 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 199.146 | 149.998 | 199.146 | 14.604 | 1574173.7816 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 149.998 | 1062.522 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 144.4774 | 1057.0014 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 135.5015 | 1048.0255 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 119.2861 | 1031.8101
[5 empty] | 226 | 912.565 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 199.105 | 149.4704 | 199.105 | 14.601 | 1573851.8574 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 149.4704 | 1062.0354 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 143.8951 | 1056.4601 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 134.8304 | 1047.3954 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 118.4544 | 1031.0194
[5 empty] | 228 | 913.484 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 198.186 | 148.0648 | 198.186 | 14.5336 | 1566635.8105 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 148.0648 | 1061.5488 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 142.4349 | 1055.9189 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 133.2813 | 1046.7653 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 116.7447 | 1030.2287
[5 empty] | 230 | 913.545 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 198.125 | 147.5172 | 198.125 | 14.5292 | 1566156.8188 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 147.5172 | 1061.0622 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 141.8326 | 1055.3776 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 132.5901 | 1046.1351 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 115.893 | 1029.438
[5 empty] | 232 | 914.546 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 197.124 | 146.0295 | 197.124 | 14.4558 | 1558296.3605 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 146.0295 | 1060.5755 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 140.2903 | 1054.8363 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 130.959 | 1045.505 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 114.1013 | 1028.6473
[5 empty] | 234 | 918.285 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 193.385 | 141.8039 | 193.385 | 14.1816 | 1528930.7669 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 141.8039 | 1060.0889 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 136.01 | 1054.295 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 126.5898 | 1044.8748 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 109.5716 | 1027.8566
[5 empty] | 236 | 919.357 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 192.313 | 140.2453 | 192.313 | 14.103 | 1520510.0578 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 140.2453 | 1059.6023 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 134.3968 | 1053.7538 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 124.8877 | 1044.2447 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 107.7089 | 1027.0659
[5 empty] | 238 | 918.649 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 193.021 | 140.4667 | 193.021 | 14.1549 | 1526071.5646 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 140.4667 | 1059.1157 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 134.5635 | 1053.2125 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 124.9655 | 1043.6145 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 107.6262 | 1026.2752
[5 empty] | 240 | 922.974 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 188.696 | 135.6551 | 188.696 | 13.8377 | 1492093.5211 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 135.6551 | 1058.6291 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 129.6972 | 1052.6712 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 120.0104 | 1042.9844 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 102.5105 | 1025.4845
[5 empty] | 242 | 927.375 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 184.295 | 130.7675 | 184.295 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 130.7675 | 1058.1425 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 124.7549 | 1052.1299 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 114.9793 | 1042.3543 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 97.3188 | 1024.6938
[5 empty] | 244 | 929.253 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 182.417 | 128.4029 | 182.417 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 128.4029 | 1057.6559 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 122.3357 | 1051.5887 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 112.4711 | 1041.7241 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 94.6501 | 1023.9031
[5 empty] | 246 | 930.863 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 180.807 | 126.3062 | 180.807 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 126.3062 | 1057.1692 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 120.1844 | 1051.0474 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 110.231 | 1041.094 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 92.2495 | 1023.1125
[5 empty] | 248 | 931.924 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 179.746 | 124.7586 | 179.746 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 124.7586 | 1056.6826 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 118.5821 | 1050.5061 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 108.5398 | 1040.4638 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 90.3978 | 1022.3218
[5 empty] | 250 | 936.722 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 174.948 | 119.474 | 174.948 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 119.474 | 1056.196 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 113.2428 | 1049.9648 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 103.1117 | 1039.8337 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 84.8091 | 1021.5311
[5 empty] | 252 | 941.777 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 169.893 | 113.9324 | 169.893 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 113.9324 | 1055.7094 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 107.6466 | 1049.4236 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 97.4265 | 1039.2035 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 78.9634 | 1020.7404
[5 empty] | 254 | 948.143 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 163.527 | 107.0798 | 163.527 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 107.0798 | 1055.2228 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 100.7393 | 1048.8823 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 90.4304 | 1038.5734 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 71.8067 | 1019.9497
[5 empty] | 256 | 955.417 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 156.253 | 99.3192 | 156.253 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 99.3192 | 1054.7362 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 92.924 | 1048.341 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 82.5263 | 1037.9433 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 63.742 | 1019.159
[5 empty] | 258 | 962.7 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 148.97 | 91.5496 | 148.97 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 91.5496 | 1054.2496 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 85.0998 | 1047.7998 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 74.6131 | 1037.3131 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 55.6683 | 1018.3683
[5 empty] | 260 | 969.281 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 142.389 | 84.4819 | 142.389 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 84.4819 | 1053.7629 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 77.9775 | 1047.2585 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 67.402 | 1036.683 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 48.2966 | 1017.5776
[5 empty] | 262 | 980.284 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 131.386 | 72.9923 | 131.386 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 72.9923 | 1053.2763 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 66.4332 | 1046.7172 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 55.7688 | 1036.0528 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 36.5029 | 1016.7869
[5 empty] | 264 | 986.551 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 125.119 | 66.2387 | 125.119 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 66.2387 | 1052.7897 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 59.6249 | 1046.1759 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 48.8717 | 1035.4227 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 29.4452 | 1015.9962
[5 empty] | 266 | 989.198 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 122.472 | 63.1051 | 122.472 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 63.1051 | 1052.3031 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 56.4367 | 1045.6347 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 45.5945 | 1034.7925 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 26.0075 | 1015.2055
[5 empty] | 268 | 994.39 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 117.28 | 57.4265 | 117.28 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 57.4265 | 1051.8165 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 50.7034 | 1045.0934 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 39.7724 | 1034.1624 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 20.0248 | 1014.4148
[5 empty] | 270 | 999.917 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 111.753 | 51.4129 | 111.753 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 51.4129 | 1051.3299 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 44.6351 | 1044.5521 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 33.6153 | 1033.5323 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 13.7071 | 1013.6241
[5 empty] | 272 | 1004.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 107.047 | 46.2203 | 107.047 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 46.2203 | 1050.8433 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 39.3878 | 1044.0108 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 28.2791 | 1032.9021 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 8.2105 | 1012.8335
|  |  |  | Reservoir | 274 | 1008.819 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 10 | 170 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 160 | 10 | 1178.819 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 160 | 170 | 1178.819 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 160 | 170 | 1178.819 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 160 | 170 | 1178.819
[5 empty] | 276 | 1007.834 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 170.4984 | 170.4437 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 170.4984 | 1178.3324 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 170.4437 | 1178.2777 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 170.3549 | 1178.1889 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 170.1943 | 1178.0283
[5 empty] | 278 | 1005.626 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 172.2198 | 172.1105 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 172.2198 | 1177.8458 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 172.1105 | 1177.7365 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 171.9327 | 1177.5587 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 171.6116 | 1177.2376
[5 empty] | 280 | 1001.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 175.7362 | 175.5722 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 175.7362 | 1177.3592 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 175.5722 | 1177.1952 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 175.3056 | 1176.9286 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 174.8239 | 1176.4469
[5 empty] | 282 | 1004.052 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 172.8205 | 172.6019 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 172.8205 | 1176.8725 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 172.6019 | 1176.6539 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 172.2464 | 1176.2984 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 171.6042 | 1175.6562
[5 empty] | 284 | 1010.797 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 165.5889 | 165.3156 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 165.5889 | 1176.3859 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 165.3156 | 1176.1126 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 164.8713 | 1175.6683 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 164.0685 | 1174.8655
[5 empty] | 286 | 1014.67 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 161.2293 | 160.9014 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 161.2293 | 1175.8993 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 160.9014 | 1175.5714 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 160.3681 | 1175.0381 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 159.4048 | 1174.0748
[5 empty] | 288 | 1017.319 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 158.0937 | 157.7111 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 158.0937 | 1175.4127 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 157.7111 | 1175.0301 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 157.089 | 1174.408 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 155.9652 | 1173.2842
[5 empty] | 290 | 1027.459 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 147.4671 | 147.0298 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 147.4671 | 1174.9261 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 147.0298 | 1174.4888 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 146.3189 | 1173.7779 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 145.0345 | 1172.4935
[5 empty] | 292 | 1031.99 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 142.4495 | 141.9575 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 142.4495 | 1174.4395 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 141.9575 | 1173.9475 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 141.1577 | 1173.1477 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 139.7128 | 1171.7028
[5 empty] | 294 | 1036.254 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 137.6989 | 137.1523 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 137.6989 | 1173.9529 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 137.1523 | 1173.4063 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 136.2636 | 1172.5176 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 134.6581 | 1170.9121
[5 empty] | 296 | 1040.127 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 133.3392 | 132.738 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 133.3392 | 1173.4662 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 132.738 | 1172.865 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 131.7604 | 1171.8874 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 129.9944 | 1170.1214
[5 empty] | 298 | 1044.396 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 128.5836 | 127.9277 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 128.5836 | 1172.9796 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 127.9277 | 1172.3237 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 126.8613 | 1171.2573 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 124.9347 | 1169.3307
[5 empty] | 300 | 1051.339 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 121.154 | 120.4434 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 121.154 | 1172.493 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 120.4434 | 1171.7824 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 119.2881 | 1170.6271 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 117.201 | 1168.54
[5 empty] | 302 | 1060.955 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 111.0514 | 110.2862 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 111.0514 | 1172.0064 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 110.2862 | 1171.2412 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 109.042 | 1169.997 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 106.7943 | 1167.7493
[5 empty] | 304 | 1070.227 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 101.2928 | 100.4729 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 101.2928 | 1171.5198 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 100.4729 | 1170.6999 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 99.1399 | 1169.3669 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 96.7316 | 1166.9586
[5 empty] | 306 | 1072.691 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 98.3422 | 97.4676 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 98.3422 | 1171.0332 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 97.4676 | 1170.1586 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 96.0457 | 1168.7367 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 93.4769 | 1166.1679
[5 empty] | 308 | 1076.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 94.0436 | 93.1144 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 94.0436 | 1170.5466 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 93.1144 | 1169.6174 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 91.6036 | 1168.1066 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 88.8742 | 1165.3772
[5 empty] | 310 | 1083.996 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 86.064 | 85.0801 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 86.064 | 1170.06 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 85.0801 | 1169.0761 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 83.4804 | 1167.4764 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 80.5905 | 1164.5865
[5 empty] | 312 | 1097.188 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 72.3853 | 71.3468 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 72.3853 | 1169.5733 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 71.3468 | 1168.5348 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 69.6583 | 1166.8463 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 66.6078 | 1163.7958
[5 empty] | 314 | 1103.545 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 65.5417 | 64.4485 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 65.5417 | 1169.0867 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 64.4485 | 1167.9935 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 62.6711 | 1166.2161 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 59.4602 | 1163.0052
[5 empty] | 316 | 1105.174 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 63.4261 | 62.2783 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 63.4261 | 1168.6001 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 62.2783 | 1167.4523 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 60.412 | 1165.586 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 57.0405 | 1162.2145
[5 empty] | 318 | 1111.657 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 56.4565 | 55.254 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 56.4565 | 1168.1135 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 55.254 | 1166.911 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 53.2989 | 1164.9559 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 49.7668 | 1161.4238
[5 empty] | 320 | 1122.935 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 44.6919 | 43.4347 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 44.6919 | 1167.6269 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 43.4347 | 1166.3697 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 41.3907 | 1164.3257 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 37.6981 | 1160.6331
[5 empty] | 322 | 1128.197 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 38.9433 | 37.6314 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 38.9433 | 1167.1403 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 37.6314 | 1165.8284 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 35.4986 | 1163.6956 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 31.6454 | 1159.8424
[5 empty] | 324 | 1132.561 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 34.0927 | 32.7262 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 34.0927 | 1166.6537 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 32.7262 | 1165.2872 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 30.5044 | 1163.0654 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 26.4907 | 1159.0517
[5 empty] | 326 | 1131.854 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 34.313 | 32.8919 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 34.313 | 1166.167 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 32.8919 | 1164.7459 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 30.5813 | 1162.4353 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 26.407 | 1158.261
[5 empty] | 328 | 1133.338 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 32.3424 | 30.8666 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 32.3424 | 1165.6804 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 30.8666 | 1164.2046 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 28.4671 | 1161.8051 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 24.1323 | 1157.4703
[5 empty] | 330 | 1136.405 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 28.7888 | 27.2583 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 28.7888 | 1165.1938 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 27.2583 | 1163.6633 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 24.77 | 1161.175 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 20.2746 | 1156.6796
[5 empty] | 332 | 1128.709 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 35.9982 | 34.4131 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 35.9982 | 1164.7072 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 34.4131 | 1163.1221 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 31.8358 | 1160.5448 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 27.1799 | 1155.8889
[5 empty] | 334 | 1120.713 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 43.5076 | 41.8678 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 43.5076 | 1164.2206 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 41.8678 | 1162.5808 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 39.2017 | 1159.9147 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 34.3852 | 1155.0982
[5 empty] | 336 | 1115.226 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 47.6436 | 45.8471 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 47.6436 | 1162.8696 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 45.8471 | 1161.0731 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 42.9253 | 1158.1513 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 37.6422 | 1152.8682
[5 empty] | 338 | 1108.709 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 52.8097 | 50.8565 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 52.8097 | 1161.5187 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 50.8565 | 1159.5655 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 47.6789 | 1156.3879 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 41.9292 | 1150.6382
[5 empty] | 340 | 1102.499 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 57.6687 | 55.5588 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 57.6687 | 1160.1677 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 55.5588 | 1158.0578 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 52.1255 | 1154.6245 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 45.9092 | 1148.4082
[5 empty] | 342 | 1096.349 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 62.4678 | 60.2011 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 62.4678 | 1158.8168 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 60.2011 | 1156.5501 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 56.5121 | 1152.8611 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 49.8292 | 1146.1782
[5 empty] | 344 | 1090.39 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 67.0758 | 64.6525 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 67.0758 | 1157.4658 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 64.6525 | 1155.0425 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 60.7077 | 1151.0977 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 53.5581 | 1143.9481
[5 empty] | 346 | 1087.765 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 68.3499 | 65.7698 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 68.3499 | 1156.1149 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 65.7698 | 1153.5348 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 61.5693 | 1149.3343 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 53.9531 | 1141.7181
[5 empty] | 348 | 1084.661 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 70.1029 | 67.3661 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 70.1029 | 1154.7639 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 67.3661 | 1152.0271 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 62.9099 | 1147.5709 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 54.8271 | 1139.4881
[5 empty] | 350 | 1081.662 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 71.751 | 68.8574 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 71.751 | 1153.413 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 68.8574 | 1150.5194 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 64.1455 | 1145.8075 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.5961 | 1137.2581
[5 empty] | 352 | 1076.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 75.19 | 72.1398 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 75.19 | 1152.062 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 72.1398 | 1149.0118 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 67.1721 | 1144.0441 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 58.1561 | 1135.0281
[5 empty] | 354 | 1070.898 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 79.813 | 76.6061 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 79.813 | 1150.711 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 76.6061 | 1147.5041 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 71.3827 | 1142.2807 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 61.9001 | 1132.7981
[5 empty] | 356 | 1065.018 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 84.3421 | 80.9784 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 84.3421 | 1149.3601 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 80.9784 | 1145.9964 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 75.4993 | 1140.5173 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 65.55 | 1130.568
[5 empty] | 358 | 1059.58 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 88.4291 | 84.9088 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 88.4291 | 1148.0091 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 84.9088 | 1144.4888 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 79.1739 | 1138.7539 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 68.758 | 1128.338
[5 empty] | 360 | 1055.284 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 91.3742 | 87.6971 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 91.3742 | 1146.6582 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 87.6971 | 1142.9811 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 81.7065 | 1136.9905 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 70.824 | 1126.108
[5 empty] | 362 | 1050.886 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 94.4212 | 90.5874 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 94.4212 | 1145.3072 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 90.5874 | 1141.4734 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 84.3412 | 1135.2272 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 72.992 | 1123.878
[5 empty] | 364 | 1052.647 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 91.3093 | 87.3188 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 91.3093 | 1143.9563 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 87.3188 | 1139.9658 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 80.8168 | 1133.4638 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 69.001 | 1121.648
[5 empty] | 366 | 1051.117 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 91.4883 | 87.3411 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 91.4883 | 1142.6053 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 87.3411 | 1138.4581 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 80.5834 | 1131.7004 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 68.301 | 1119.418
[5 empty] | 368 | 1048.266 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 92.9884 | 88.6844 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 92.9884 | 1141.2544 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 88.6844 | 1136.9504 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 81.671 | 1129.937 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 68.9219 | 1117.1879
[5 empty] | 370 | 1040.172 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 99.7314 | 95.2708 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 99.7314 | 1139.9034 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 95.2708 | 1135.4428 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 88.0016 | 1128.1736 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 74.7859 | 1114.9579
[5 empty] | 372 | 1033.483 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 105.0695 | 100.4521 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 105.0695 | 1138.5525 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 100.4521 | 1133.9351 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 92.9272 | 1126.4102 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 79.2449 | 1112.7279
[5 empty] | 374 | 1030.95 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 106.2515 | 101.4774 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 106.2515 | 1137.2015 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 101.4774 | 1132.4274 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 93.6968 | 1124.6468 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 79.5479 | 1110.4979
[5 empty] | 376 | 1032.263 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 103.5876 | 98.6567 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 103.5876 | 1135.8506 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 98.6567 | 1130.9197 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 90.6204 | 1122.8834 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 76.0049 | 1108.2679
[5 empty] | 378 | 1031.391 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 103.1086 | 98.0211 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 103.1086 | 1134.4996 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 98.0211 | 1129.4121 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 89.729 | 1121.12 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 74.6469 | 1106.0379
[5 empty] | 380 | 1025.791 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 107.3576 | 102.1134 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 107.3576 | 1133.1486 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 102.1134 | 1127.9044 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 93.5656 | 1119.3566 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 78.0169 | 1103.8079
[5 empty] | 382 | 1020.911 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 110.8867 | 105.4857 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 110.8867 | 1131.7977 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 105.4857 | 1126.3967 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 96.6822 | 1117.5932 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 80.6668 | 1101.5778
[5 empty] | 384 | 1015.65 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 114.7967 | 109.2391 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 114.7967 | 1130.4467 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 109.2391 | 1124.8891 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 100.1798 | 1115.8298 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 83.6978 | 1099.3478
[5 empty] | 386 | 1012.139 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 116.9568 | 111.2424 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 116.9568 | 1129.0958 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 111.2424 | 1123.3814 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 101.9274 | 1114.0664 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 84.9788 | 1097.1178
[5 empty] | 388 | 1010.472 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 117.2728 | 111.4017 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 117.2728 | 1127.7448 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 111.4017 | 1121.8737 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 101.831 | 1112.303 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 84.4158 | 1094.8878
[5 empty] | 390 | 1005.401 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 120.9929 | 114.9651 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 120.9929 | 1126.3939 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 114.9651 | 1120.3661 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 105.1386 | 1110.5396 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 87.2568 | 1092.6578
[5 empty] | 392 | 996.666 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 128.3769 | 122.1924 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 128.3769 | 1125.0429 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 122.1924 | 1118.8584 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 112.1102 | 1108.7762 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 93.7618 | 1090.4278
[5 empty] | 394 | 991.35 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 132.342 | 126.0007 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 132.342 | 1123.692 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 126.0007 | 1117.3507 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 115.6628 | 1107.0128 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 96.8477 | 1088.1977
[5 empty] | 396 | 990.486 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 131.855 | 125.3571 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 131.855 | 1122.341 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 125.3571 | 1115.8431 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 114.7634 | 1105.2494 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 95.4817 | 1085.9677
[5 empty] | 398 | 992.761 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 128.2291 | 121.5744 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 128.2291 | 1120.9901 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 121.5744 | 1114.3354 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 110.725 | 1103.486 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 90.9767 | 1083.7377
[5 empty] | 400 | 999.077 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 120.5621 | 113.7507 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 120.5621 | 1119.6391 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 113.7507 | 1112.8277 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 102.6456 | 1101.7226 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 82.4307 | 1081.5077
[5 empty] | 402 | 1001.8 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 116.4882 | 109.52 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 116.4882 | 1118.2882 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 109.52 | 1111.32 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 98.1592 | 1099.9592 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 77.4777 | 1079.2777
[5 empty] | 404 | 1002.224 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 114.7132 | 107.5884 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 114.7132 | 1116.9372 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 107.5884 | 1109.8124 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 95.9718 | 1098.1958 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 74.8237 | 1077.0477
[5 empty] | 406 | 1002.003 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 113.5833 | 106.3017 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 113.5833 | 1115.5863 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 106.3017 | 1108.3047 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 94.4294 | 1096.4324 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 72.8146 | 1074.8176
[5 empty] | 408 | 1003.596 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 110.6393 | 103.201 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 110.6393 | 1114.2353 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 103.201 | 1106.797 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 91.073 | 1094.669 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 68.9916 | 1072.5876
[5 empty] | 410 | 994.111 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 118.7733 | 111.1784 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 118.7733 | 1112.8843 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 111.1784 | 1105.2894 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 98.7946 | 1092.9056 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 76.2466 | 1070.3576
[5 empty] | 412 | 983.925 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 127.6084 | 119.8567 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 127.6084 | 1111.5334 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 119.8567 | 1103.7817 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 107.2172 | 1091.1422 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 84.2026 | 1068.1276
[5 empty] | 414 | 972.347 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 137.8354 | 129.927 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 137.8354 | 1110.1824 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 129.927 | 1102.274 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 117.0318 | 1089.3788 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 93.5506 | 1065.8976
[5 empty] | 416 | 963.901 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 144.9305 | 136.8654 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 144.9305 | 1108.8315 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 136.8654 | 1100.7664 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 123.7144 | 1087.6154 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 99.7666 | 1063.6676
[5 empty] | 418 | 963.258 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 144.2225 | 136.0007 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 144.2225 | 1107.4805 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 136.0007 | 1099.2587 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 122.594 | 1085.852 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 98.1795 | 1061.4375
[5 empty] | 420 | 965.836 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 140.2936 | 131.915 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 140.2936 | 1106.1296 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 131.915 | 1097.751 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 118.2526 | 1084.0886 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 93.3715 | 1059.2075
[5 empty] | 422 | 966.309 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 138.4696 | 129.9344 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 138.4696 | 1104.7786 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 129.9344 | 1096.2434 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 116.0162 | 1082.3252 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 90.6685 | 1056.9775
[5 empty] | 424 | 972.884 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 130.5437 | 121.8517 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 130.5437 | 1103.4277 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 121.8517 | 1094.7357 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 107.6779 | 1080.5619 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 81.8635 | 1054.7475
[5 empty] | 426 | 983.972 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 118.1047 | 109.256 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 118.1047 | 1102.0767 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 109.256 | 1093.228 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 94.8265 | 1078.7985 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 68.5455 | 1052.5175
[5 empty] | 428 | 994.096 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 106.6298 | 97.6243 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 106.6298 | 1100.7258 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 97.6243 | 1091.7203 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 82.9391 | 1077.0351 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 56.1915 | 1050.2875
[5 empty] | 430 | 991.695 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 107.6798 | 98.5177 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 107.6798 | 1099.3748 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 98.5177 | 1090.2127 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 83.5767 | 1075.2717 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 56.3624 | 1048.0574
[5 empty] | 432 | 984.933 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 113.0909 | 103.772 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 113.0909 | 1098.0239 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 103.772 | 1088.705 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 88.5753 | 1073.5083 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 60.8944 | 1045.8274
[5 empty] | 434 | 978.185 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 118.4879 | 109.0123 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 118.4879 | 1096.6729 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 109.0123 | 1087.1973 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 93.5599 | 1071.7449 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 65.4124 | 1043.5974
[5 empty] | 436 | 972.686 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 122.6359 | 113.0037 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 122.6359 | 1095.3219 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 113.0037 | 1085.6897 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 97.2955 | 1069.9815 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 68.6814 | 1041.3674
[5 empty] | 438 | 966.824 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 127.147 | 117.358 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 127.147 | 1093.971 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 117.358 | 1084.182 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 101.3941 | 1068.2181 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 72.3134 | 1039.1374
[5 empty] | 440 | 960.902 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 131.718 | 121.7723 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 131.718 | 1092.62 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 121.7723 | 1082.6743 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 105.5527 | 1066.4547 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 76.0054 | 1036.9074
[5 empty] | 442 | 952.924 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 138.3451 | 128.2427 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 138.3451 | 1091.2691 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 128.2427 | 1081.1667 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 111.7673 | 1064.6913 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 81.7533 | 1034.6773
[5 empty] | 444 | 945.683 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 144.2351 | 133.976 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 144.2351 | 1089.9181 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 133.976 | 1079.659 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 117.2449 | 1062.9279 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 86.7643 | 1032.4473
[5 empty] | 446 | 941.042 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 147.5252 | 137.1093 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 147.5252 | 1088.5672 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 137.1093 | 1078.1513 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 120.1225 | 1061.1645 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 89.1753 | 1030.2173
[5 empty] | 448 | 937.104 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 150.1122 | 139.5397 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 150.1122 | 1087.2162 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 139.5397 | 1076.6437 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 122.2971 | 1059.4011 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 90.8833 | 1027.9873
[5 empty] | 450 | 939.943 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 145.9223 | 135.193 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 145.9223 | 1085.8653 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 135.193 | 1075.136 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 117.6947 | 1057.6377 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 85.8143 | 1025.7573
[5 empty] | 452 | 944.776 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 139.7383 | 128.8523 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 139.7383 | 1084.5143 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 128.8523 | 1073.6283 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 111.0983 | 1055.8743 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 78.7513 | 1023.5273
[5 empty] | 454 | 947.762 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 135.4014 | 124.3586 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 135.4014 | 1083.1634 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 124.3586 | 1072.1206 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 106.3489 | 1054.1109 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 73.5352 | 1021.2972
[5 empty] | 456 | 952.649 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 129.1634 | 117.964 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 129.1634 | 1081.8124 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 117.964 | 1070.613 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 99.6985 | 1052.3475 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 66.4182 | 1019.0672
[5 empty] | 458 | 954.554 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 125.9075 | 114.5513 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 125.9075 | 1080.4615 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 114.5513 | 1069.1053 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 96.0301 | 1050.5841 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 62.2832 | 1016.8372
[5 empty] | 460 | 952.37 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 126.7405 | 115.2276 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 126.7405 | 1079.1105 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 115.2276 | 1067.5976 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 96.4507 | 1048.8207 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 62.2372 | 1014.6072
[5 empty] | 462 | 947.552 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 130.2075 | 118.538 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 130.2075 | 1077.7595 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 118.538 | 1066.09 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 99.5053 | 1047.0573 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 64.8252 | 1012.3772
[5 empty] | 464 | 941.898 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 134.5106 | 122.6843 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 134.5106 | 1076.4086 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 122.6843 | 1064.5823 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 103.3959 | 1045.2939 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 68.2492 | 1010.1472
[5 empty] | 466 | 940.521 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 134.5366 | 122.5536 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 134.5366 | 1075.0576 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 122.5536 | 1063.0746 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 103.0095 | 1043.5305 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 67.3961 | 1007.9171
[5 empty] | 468 | 939.702 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 134.0047 | 121.865 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 134.0047 | 1073.7067 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 121.865 | 1061.567 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 102.0651 | 1041.7671 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 65.9851 | 1005.6871
[5 empty] | 470 | 937.147 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 135.2087 | 122.9123 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 135.2087 | 1072.3557 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 122.9123 | 1060.0593 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 102.8567 | 1040.0037 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 66.3101 | 1003.4571
[5 empty] | 472 | 933.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 137.1328 | 124.6796 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 137.1328 | 1071.0048 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 124.6796 | 1058.5516 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 104.3683 | 1038.2403 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 67.3551 | 1001.2271
[5 empty] | 474 | 933.184 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 136.4698 | 123.86 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 136.4698 | 1069.6538 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 123.86 | 1057.044 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 103.2929 | 1036.4769 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 65.8131 | 998.9971
[5 empty] | 476 | 939.292 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 129.0109 | 116.2443 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 129.0109 | 1068.3029 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 116.2443 | 1055.5363 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 95.4215 | 1034.7135 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 57.4751 | 996.7671
[5 empty] | 478 | 944.619 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 122.3329 | 109.4096 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 122.3329 | 1066.9519 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 109.4096 | 1054.0286 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 88.3311 | 1032.9501 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 49.918 | 994.537
[5 empty] | 480 | 954.023 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 111.578 | 98.4979 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 111.578 | 1065.601 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 98.4979 | 1052.5209 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 77.1637 | 1031.1867 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 38.284 | 992.307
[5 empty] | 482 | 968.263 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 95.987 | 82.7503 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 95.987 | 1064.25 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 82.7503 | 1051.0133 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 61.1603 | 1029.4233 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 21.814 | 990.077
[5 empty] | 484 | 970.384 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 92.5151 | 79.1216 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 92.5151 | 1062.8991 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 79.1216 | 1049.5056 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 57.2759 | 1027.6599 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 17.463 | 987.847
[5 empty] | 486 | 964.636 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 96.9121 | 83.3619 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 96.9121 | 1061.5481 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 83.3619 | 1047.9979 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 61.2605 | 1025.8965 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 20.981 | 985.617
[5 empty] | 488 | 956.631 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 103.5661 | 89.8593 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 103.5661 | 1060.1971 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 89.8593 | 1046.4903 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 67.5022 | 1024.1332 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 26.756 | 983.387
[5 empty] | 490 | 947.426 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 111.4202 | 97.5566 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 111.4202 | 1058.8462 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 97.5566 | 1044.9826 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 74.9438 | 1022.3698 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 33.7309 | 981.1569
[5 empty] | 492 | 941.72 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 115.7752 | 101.7549 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 115.7752 | 1057.4952 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 101.7549 | 1043.4749 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 78.8864 | 1020.6064 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 37.2069 | 978.9269
[5 empty] | 494 | 935.985 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 120.1593 | 105.9823 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 120.1593 | 1056.1443 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 105.9823 | 1041.9673 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 82.858 | 1018.843 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 40.7119 | 976.6969
[5 empty] | 496 | 930.475 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 124.3183 | 109.9846 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 124.3183 | 1054.7933 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 109.9846 | 1040.4596 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 86.6046 | 1017.0796 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 43.9919 | 974.4669
[5 empty] | 498 | 927.611 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 125.8314 | 111.3409 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 125.8314 | 1053.4424 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 111.3409 | 1038.9519 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 87.7052 | 1015.3162 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 44.6259 | 972.2369
[5 empty] | 500 | 931.256 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 120.8354 | 106.1883 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 120.8354 | 1052.0914 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 106.1883 | 1037.4443 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 82.2968 | 1013.5528 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 38.7509 | 970.0069
[5 empty] | 502 | 920.044 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 130.6965 | 115.8926 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 130.6965 | 1050.7405 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 115.8926 | 1035.9366 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 91.7454 | 1011.7894 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 47.7328 | 967.7768
[5 empty] | 504 | 911.78 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 137.6095 | 122.6489 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 137.6095 | 1049.3895 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 122.6489 | 1034.4289 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 98.246 | 1010.026 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 53.7668 | 965.5468
[5 empty] | 506 | 907.989 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 140.0496 | 124.9322 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 140.0496 | 1048.0386 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 124.9322 | 1032.9212 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 100.2736 | 1008.2626 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.3278 | 963.3168
[5 empty] | 508 | 907.289 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 137.3232 | 121.7976 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 137.3232 | 1044.6122 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 121.7976 | 1029.0866 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 96.4702 | 1003.7592 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 50.2922 | 957.5812
[5 empty] | 510 | 900.577 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 140.6089 | 124.6749 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 140.6089 | 1041.1859 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 124.6749 | 1025.2519 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 98.6789 | 999.2559 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 51.2685 | 951.8455
[5 empty] | 512 | 902.112 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 135.6476 | 119.3052 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 135.6476 | 1037.7596 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 119.3052 | 1021.4172 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 92.6406 | 994.7526 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 43.9978 | 946.1098
[5 empty] | 514 | 900.179 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 134.1542 | 117.4035 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 134.1542 | 1034.3332 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 117.4035 | 1017.5825 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 90.0702 | 990.2492 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 40.1952 | 940.3742
[5 empty] | 516 | 903.811 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 127.0959 | 109.9368 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 127.0959 | 1030.9069 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 109.9368 | 1013.7478 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 81.9349 | 985.7459 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 30.8275 | 934.6385
[5 empty] | 518 | 910.027 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 117.4536 | 99.8861 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 117.4536 | 1027.4806 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 99.8861 | 1009.9131 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 71.2155 | 981.2425 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 18.8759 | 928.9029
|  |  |  | Reservoir | 520 | 911.131 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 10 | 10 | 10 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 10 | 921.131 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 10 | 921.131 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 10 | 921.131 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 10 | 921.131
[15 empty] | Total Steel Mass (kg): | 333690430.228