## Cost Estimates
Air Valve, Scour Valve & Isolating Budget |  |  |  | Steel Pipe Prices |  | Pump Station Costs - DWA 2003 Escalated to 2010 |  | Electricity Costs | Pula | Rand | Reservoir Costing |  | Minor Loss - k | 150 | Pipe Trench Excavation & Back Fill
Pipe Diameter (mm) | Civil Rate/m | Mechanical Rate/m | Total R/m | Coating Cost Per m2 | 200 | PS Capacity kW | Cost R/kW | Fixed Charge Per Month | 26.09 | 28.699 | Reservoir (incl. earthowrks and lining) per m3 | 80 |  |  | Excavation Cost (R/m3) | 50
500 | 40 | 70 | 110 | Steel Pipe Cost Per Ton | 17.5 | 100 | 30227.6622 | Energy Charge Per kWh | 0.4096 | 0.45056 |  |  | Friction Factors |  | Bedding and Cradle Fill (R/m3) | 165
600 | 40 | 80 | 120 | Delivery Cost Per m | 85 | 200 | 25032.9622 | [5 empty] | Ks (mm) - New | 0.03 | Main Fill (R/m3) | 55
700 | 40 | 100 | 140 | Laying and Joining 20% of Pipe Price |  | 300 | 22423.6676 | [5 empty] | Ks (mm) - Average | 0.06 | Spoil (R/m3) | 45
800 | 40 | 140 | 180 |  |  | 400 | 20740.1478 | [5 empty] | Ks (mm) - Old | 0.15
900 | 40 | 190 | 230 |  |  | 500 | 19523.2464 | [5 empty] | Ks (mm) - Biofilm | 0.5
1000 | 40 | 250 | 290 |  |  | 600 | 18582.6012
1100 | 40 | 360 | 400 |  |  | 700 | 17823.054
1200 | 50 | 460 | 510 |  |  | 800 | 17190.3824
1300 | 50 | 480 | 530 |  |  | 900 | 16651.2418
1400 | 50 | 500 | 550 |  |  | 1000 | 16183.5318
1500 | 50 | 530 | 580 |  |  | 2000 | 13420.2993
1600 | 60 | 560 | 620 |  |  | 3000 | 12030.295
1700 | 60 | 580 | 640 |  |  | 5000 | 10484.1624
1800 | 60 | 600 | 660 |  |  | 6000 | 9982.2899
1900 | 70 | 640 | 710 |  |  | 7000 | 9576.9667
2000 | 70 | 680 | 750 |  |  | 8000 | 9239.3348
2100 | 70 | 720 | 790 |  |  | 9000 | 8951.5188
2200 | 80 | 760 | 840 |  |  | 10000 | 8701.7305
2300 | 80 | 770 | 850 |  |  | 20000 | 7225.0136
2400 | 90 | 810 | 900 |  |  | 40000 | 6001.0824
2500 | 90 | 850 | 940 |  |  | 50000 | 5653.4377
[6 empty] | 60000 | 5384.5442
[6 empty] | 70000 | 5167.2937
[6 empty] | 80000 | 4986.2759
[6 empty] | 90000 | 4831.929
[6 empty] | 100000 | 4697.9511

## Pipeline Pricing
Option 1B Pipeline Pricing
Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Pipe Wall thickness (mm) | Steel Mass (kg) | Pipe Area (m2) | Coating Cost | Delivery Cost | Pipe Cost | Chamber Cost R/m | Chamber Cost R | Pumpstation Name | Pump Station Power | Reservoir Name | Volume m3
2 | 1069.018 | 0 | 2.2 | 13.75 | 0 | 0 | 0 | 0 | 0 | 840 | 0 | PS1 | 9367
4 | 1067.321 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
6 | 1064.035 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
8 | 1063.832 | 2 | 2.2 | 15.6609 | 1687279.6635 | 13823.0077 | 2764601.5352 | 170000 | 29527394.1121 | 840 | 1680000
10 | 1067.893 | 2 | 2.2 | 15.3233 | 1651162.4615 | 13823.0077 | 2764601.5352 | 170000 | 28895343.0771 | 840 | 1680000
12 | 1075.133 | 2 | 2.2 | 14.7526 | 1590079.2461 | 13823.0077 | 2764601.5352 | 170000 | 27826386.8064 | 840 | 1680000
14 | 1082.768 | 2 | 2.2 | 14.1529 | 1525861.1907 | 13823.0077 | 2764601.5352 | 170000 | 26702570.837 | 840 | 1680000
16 | 1089.726 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
18 | 1094.131 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
20 | 1097.897 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
22 | 1101.67 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
24 | 1095.952 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
26 | 1090.107 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
28 | 1085.781 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
30 | 1081.89 | 2 | 2.2 | 13.899 | 1498655.5949 | 13823.0077 | 2764601.5352 | 170000 | 26226472.9108 | 840 | 1680000
32 | 1077.937 | 2 | 2.2 | 14.149 | 1525447.4405 | 13823.0077 | 2764601.5352 | 170000 | 26695330.2088 | 840 | 1680000
34 | 1074.89 | 2 | 2.2 | 14.3327 | 1545117.826 | 13823.0077 | 2764601.5352 | 170000 | 27039561.9548 | 840 | 1680000
36 | 1071.114 | 2 | 2.2 | 14.5698 | 1570509.1669 | 13823.0077 | 2764601.5352 | 170000 | 27483910.4199 | 840 | 1680000
38 | 1065.311 | 2 | 2.2 | 14.9556 | 1611806.4923 | 13823.0077 | 2764601.5352 | 170000 | 28206613.6156 | 840 | 1680000
40 | 1059.051 | 2 | 2.2 | 15.3748 | 1656674.9172 | 13823.0077 | 2764601.5352 | 170000 | 28991811.0514 | 840 | 1680000
42 | 1054.28 | 2 | 2.2 | 15.6849 | 1689846.904 | 13823.0077 | 2764601.5352 | 170000 | 29572320.8192 | 840 | 1680000
44 | 1053.871 | 2 | 2.2 | 15.6751 | 1688798.7057 | 13823.0077 | 2764601.5352 | 170000 | 29553977.3492 | 840 | 1680000
46 | 1050.42 | 2 | 2.2 | 15.8884 | 1711609.8598 | 13823.0077 | 2764601.5352 | 170000 | 29953172.5467 | 840 | 1680000
48 | 1052.704 | 2 | 2.2 | 15.6811 | 1689439.8714 | 13823.0077 | 2764601.5352 | 170000 | 29565197.7493 | 840 | 1680000
50 | 1056.355 | 2 | 2.2 | 15.3736 | 1656540.3415 | 13823.0077 | 2764601.5352 | 170000 | 28989455.976 | 840 | 1680000
52 | 1058.466 | 2 | 2.2 | 15.179 | 1635717.4756 | 13823.0077 | 2764601.5352 | 170000 | 28625055.823 | 840 | 1680000
54 | 1055.99 | 2 | 2.2 | 15.3208 | 1650888.872 | 13823.0077 | 2764601.5352 | 170000 | 28890555.2591 | 840 | 1680000
56 | 1055.66 | 2 | 2.2 | 15.3052 | 1649220.4319 | 13823.0077 | 2764601.5352 | 170000 | 28861357.5583 | 840 | 1680000
58 | 1056.404 | 2 | 2.2 | 15.2108 | 1639124.1565 | 13823.0077 | 2764601.5352 | 170000 | 28684672.7395 | 840 | 1680000
60 | 1056.841 | 2 | 2.2 | 15.139 | 1631436.3421 | 13823.0077 | 2764601.5352 | 170000 | 28550135.9868 | 840 | 1680000
62 | 1056.377 | 2 | 2.2 | 15.1332 | 1630819.2552 | 13823.0077 | 2764601.5352 | 170000 | 28539336.9667 | 840 | 1680000
64 | 1052.503 | 2 | 2.2 | 15.3775 | 1656960.8021 | 13823.0077 | 2764601.5352 | 170000 | 28996814.0376 | 840 | 1680000
66 | 1046.022 | 2 | 2.2 | 15.813 | 1703545.1032 | 13823.0077 | 2764601.5352 | 170000 | 29812039.3051 | 840 | 1680000
68 | 1036.575 | 2 | 2.2 | 16.466 | 1773361.5142 | 13823.0077 | 2764601.5352 | 170000 | 31033826.4989 | 840 | 1680000
70 | 1031.818 | 2 | 2.2 | 16.775 | 1806390.4197 | 13823.0077 | 2764601.5352 | 170000 | 31611832.3448 | 840 | 1680000
72 | 1027.675 | 2 | 2.2 | 17.0391 | 1834599.8145 | 13823.0077 | 2764601.5352 | 170000 | 32105496.7529 | 840 | 1680000
74 | 1023.844 | 2 | 2.2 | 17.2802 | 1860358.6374 | 13823.0077 | 2764601.5352 | 170000 | 32556276.1549 | 840 | 1680000
76 | 1020.888 | 2 | 2.2 | 17.4572 | 1879259.6632 | 13823.0077 | 2764601.5352 | 170000 | 32887044.1054 | 840 | 1680000
78 | 1023.648 | 2 | 2.2 | 17.215 | 1853393.3478 | 13823.0077 | 2764601.5352 | 170000 | 32434383.5869 | 840 | 1680000
80 | 1027.566 | 2 | 2.2 | 16.8879 | 1818448.351 | 13823.0077 | 2764601.5352 | 170000 | 31822846.1426 | 840 | 1680000
82 | 1032.371 | 2 | 2.2 | 16.4957 | 1776540.6004 | 13823.0077 | 2764601.5352 | 170000 | 31089460.5068 | 840 | 1680000
84 | 1034.983 | 2 | 2.2 | 16.2644 | 1751811.6087 | 13823.0077 | 2764601.5352 | 170000 | 30656703.152 | 840 | 1680000
86 | 1033.213 | 2 | 2.2 | 16.3544 | 1761433.5265 | 13823.0077 | 2764601.5352 | 170000 | 30825086.7134 | 840 | 1680000
88 | 1031.188 | 2 | 2.2 | 16.4631 | 1773053.4416 | 13823.0077 | 2764601.5352 | 170000 | 31028435.2282 | 840 | 1680000
90 | 1029.08 | 2 | 2.2 | 16.5779 | 1785322.707 | 13823.0077 | 2764601.5352 | 170000 | 31243147.3719 | 840 | 1680000
92 | 1026.322 | 2 | 2.2 | 16.7404 | 1802684.4083 | 13823.0077 | 2764601.5352 | 170000 | 31546977.1447 | 840 | 1680000
94 | 1023.207 | 2 | 2.2 | 16.929 | 1822840.6275 | 13823.0077 | 2764601.5352 | 170000 | 31899710.9816 | 840 | 1680000
96 | 1021.503 | 2 | 2.2 | 17.0142 | 1831939.5775 | 13823.0077 | 2764601.5352 | 170000 | 32058942.6066 | 840 | 1680000
98 | 1019.765 | 2 | 2.2 | 17.1018 | 1841304.1591 | 13823.0077 | 2764601.5352 | 170000 | 32222822.7843 | 840 | 1680000
100 | 1018.493 | 2 | 2.2 | 17.1553 | 1847017.7026 | 13823.0077 | 2764601.5352 | 170000 | 32322809.7963 | 840 | 1680000
102 | 1016.444 | 2 | 2.2 | 17.2658 | 1858817.0103 | 13823.0077 | 2764601.5352 | 170000 | 32529297.6806 | 840 | 1680000
104 | 1013.288 | 2 | 2.2 | 17.4574 | 1879284.5301 | 13823.0077 | 2764601.5352 | 170000 | 32887479.2762 | 840 | 1680000
106 | 1007.843 | 2 | 2.2 | 17.8169 | 1917669.3819 | 13823.0077 | 2764601.5352 | 170000 | 33559214.1824 | 840 | 1680000
108 | 1001.282 | 2 | 2.2 | 18.2583 | 1964774.9202 | 13823.0077 | 2764601.5352 | 170000 | 34383561.1037 | 840 | 1680000
110 | 996.609 | 2 | 2.2 | 18.5612 | 1997092.0395 | 13823.0077 | 2764601.5352 | 170000 | 34949110.6913 | 840 | 1680000
112 | 992.999 | 2 | 2.2 | 18.7861 | 2021086.1057 | 13823.0077 | 2764601.5352 | 170000 | 35369006.8501 | 840 | 1680000
114 | 993.639 | 2 | 2.2 | 18.6994 | 2011835.7381 | 13823.0077 | 2764601.5352 | 170000 | 35207125.4175 | 840 | 1680000
116 | 994.611 | 2 | 2.2 | 18.5883 | 1999987.4298 | 13823.0077 | 2764601.5352 | 170000 | 34999780.0211 | 840 | 1680000
118 | 995.751 | 2 | 2.2 | 18.4649 | 1986823.5019 | 13823.0077 | 2764601.5352 | 170000 | 34769411.284 | 840 | 1680000
120 | 996.479 | 2 | 2.2 | 18.3717 | 1976881.8288 | 13823.0077 | 2764601.5352 | 170000 | 34595432.0039 | 840 | 1680000
122 | 996.147 | 2 | 2.2 | 18.3563 | 1975233.731 | 13823.0077 | 2764601.5352 | 170000 | 34566590.2924 | 840 | 1680000
124 | 992.094 | 2 | 2.2 | 18.6137 | 2002697.8924 | 13823.0077 | 2764601.5352 | 170000 | 35047213.1165 | 840 | 1680000
126 | 985.623 | 2 | 2.2 | 19.0485 | 2049064.9746 | 13823.0077 | 2764601.5352 | 170000 | 35858637.0562 | 840 | 1680000
128 | 977.759 | 2 | 2.2 | 19.5854 | 2106301.2854 | 13823.0077 | 2764601.5352 | 170000 | 36860272.494 | 840 | 1680000
130 | 969.772 | 2 | 2.2 | 20.1313 | 2164470.0174 | 13823.0077 | 2764601.5352 | 170000 | 37878225.3037 | 840 | 1680000
132 | 981.785 | 2 | 2.2 | 19.2105 | 2066345.952 | 13823.0077 | 2764601.5352 | 170000 | 36161054.16 | 840 | 1680000
134 | 991.458 | 2 | 2.2 | 18.4614 | 1986447.622 | 13823.0077 | 2764601.5352 | 170000 | 34762833.3853 | 840 | 1680000
136 | 987.77 | 2 | 2.2 | 18.6921 | 2011054.0374 | 13823.0077 | 2764601.5352 | 170000 | 35193445.6544 | 840 | 1680000
138 | 982.725 | 2 | 2.2 | 19.0222 | 2046267.2118 | 13823.0077 | 2764601.5352 | 170000 | 35809676.2063 | 840 | 1680000
140 | 977.559 | 2 | 2.2 | 19.3613 | 2082415.5397 | 13823.0077 | 2764601.5352 | 170000 | 36442271.945 | 840 | 1680000
142 | 975.289 | 2 | 2.2 | 19.488 | 2095918.261 | 13823.0077 | 2764601.5352 | 170000 | 36678569.5682 | 840 | 1680000
144 | 973.968 | 2 | 2.2 | 19.545 | 2102002.202 | 13823.0077 | 2764601.5352 | 170000 | 36785038.5352 | 840 | 1680000
146 | 962.473 | 2 | 2.2 | 20.3482 | 2187574.7097 | 13823.0077 | 2764601.5352 | 170000 | 38282557.4199 | 840 | 1680000
148 | 951.285 | 2 | 2.2 | 21.1289 | 2270687.5956 | 13823.0077 | 2764601.5352 | 170000 | 39737032.9223 | 840 | 1680000
150 | 948.174 | 2 | 2.2 | 21.3172 | 2290730.9377 | 13823.0077 | 2764601.5352 | 170000 | 40087791.4095 | 840 | 1680000
152 | 944.641 | 2 | 2.2 | 21.5365 | 2314063.1234 | 13823.0077 | 2764601.5352 | 170000 | 40496104.6592 | 840 | 1680000
154 | 941.566 | 2 | 2.2 | 21.7222 | 2333818.081 | 13823.0077 | 2764601.5352 | 170000 | 40841816.4178 | 840 | 1680000
156 | 940.942 | 2 | 2.2 | 21.7282 | 2334452.7875 | 13823.0077 | 2764601.5352 | 170000 | 40852923.7818 | 840 | 1680000
158 | 939.726 | 2 | 2.2 | 21.7776 | 2339705.1272 | 13823.0077 | 2764601.5352 | 170000 | 40944839.7264 | 840 | 1680000
160 | 936.738 | 2 | 2.2 | 21.9569 | 2358777.1921 | 13823.0077 | 2764601.5352 | 170000 | 41278600.8609 | 840 | 1680000
162 | 933.65 | 2 | 2.2 | 22.1436 | 2378625.813 | 13823.0077 | 2764601.5352 | 170000 | 41625951.7273 | 840 | 1680000
164 | 932.745 | 2 | 2.2 | 22.1701 | 2381451.2677 | 13823.0077 | 2764601.5352 | 170000 | 41675397.1855 | 840 | 1680000
166 | 931.696 | 2 | 2.2 | 22.2073 | 2385399.397 | 13823.0077 | 2764601.5352 | 170000 | 41744489.448 | 840 | 1680000
168 | 930.999 | 2 | 2.2 | 22.2186 | 2386602.9796 | 13823.0077 | 2764601.5352 | 170000 | 41765552.1432 | 840 | 1680000
170 | 930.885 | 2 | 2.2 | 22.1872 | 2383261.0225 | 13823.0077 | 2764601.5352 | 170000 | 41707067.8941 | 840 | 1680000
172 | 930.378 | 2 | 2.2 | 22.1845 | 2382983.2146 | 13823.0077 | 2764601.5352 | 170000 | 41702206.2549 | 840 | 1680000
174 | 931.324 | 2 | 2.2 | 22.0754 | 2371375.8343 | 13823.0077 | 2764601.5352 | 170000 | 41499077.1 | 840 | 1680000
176 | 933.53 | 2 | 2.2 | 21.8738 | 2349940.6965 | 13823.0077 | 2764601.5352 | 170000 | 41123962.1886 | 840 | 1680000
178 | 932.714 | 2 | 2.2 | 21.8939 | 2352072.7438 | 13823.0077 | 2764601.5352 | 170000 | 41161273.0164 | 840 | 1680000
180 | 928.311 | 2 | 2.2 | 22.1769 | 2382176.06 | 13823.0077 | 2764601.5352 | 170000 | 41688081.0507 | 840 | 1680000
182 | 924.179 | 2 | 2.2 | 22.4402 | 2410159.0148 | 13823.0077 | 2764601.5352 | 170000 | 42177782.7591 | 840 | 1680000
184 | 928.398 | 2 | 2.2 | 22.091 | 2373035.5606 | 13823.0077 | 2764601.5352 | 170000 | 41528122.3109 | 840 | 1680000
186 | 930.866 | 2 | 2.2 | 21.8702 | 2349557.3519 | 13823.0077 | 2764601.5352 | 170000 | 41117253.6578 | 840 | 1680000
188 | 928.411 | 2 | 2.2 | 22.0104 | 2364471.402 | 13823.0077 | 2764601.5352 | 170000 | 41378249.5343 | 840 | 1680000
190 | 927.849 | 2 | 2.2 | 22.0119 | 2364622.4508 | 13823.0077 | 2764601.5352 | 170000 | 41380892.8892 | 840 | 1680000
192 | 926.71 | 2 | 2.2 | 22.0556 | 2369272.9724 | 13823.0077 | 2764601.5352 | 170000 | 41462277.0175 | 840 | 1680000
194 | 926.201 | 2 | 2.2 | 22.0531 | 2369010.7264 | 13823.0077 | 2764601.5352 | 170000 | 41457687.7119 | 840 | 1680000
196 | 924.509 | 2 | 2.2 | 22.1374 | 2377973.059 | 13823.0077 | 2764601.5352 | 170000 | 41614528.5321 | 840 | 1680000
198 | 923.417 | 2 | 2.2 | 22.1777 | 2382256.58 | 13823.0077 | 2764601.5352 | 170000 | 41689490.1505 | 840 | 1680000
200 | 923.011 | 2 | 2.2 | 22.1677 | 2381191.267 | 13823.0077 | 2764601.5352 | 170000 | 41670847.1721 | 840 | 1680000
202 | 921.969 | 2 | 2.2 | 22.2043 | 2385084.8275 | 13823.0077 | 2764601.5352 | 170000 | 41738984.4815 | 840 | 1680000
204 | 920.661 | 2 | 2.2 | 22.2604 | 2391052.1201 | 13823.0077 | 2764601.5352 | 170000 | 41843412.1015 | 840 | 1680000
206 | 920.243 | 2 | 2.2 | 22.2513 | 2390080.4466 | 13823.0077 | 2764601.5352 | 170000 | 41826407.8151 | 840 | 1680000
208 | 919.297 | 2 | 2.2 | 22.2809 | 2393225.2662 | 13823.0077 | 2764601.5352 | 170000 | 41881442.1581 | 840 | 1680000
210 | 917.533 | 2 | 2.2 | 22.3704 | 2402746.9909 | 13823.0077 | 2764601.5352 | 170000 | 42048072.3408 | 840 | 1680000
212 | 917.684 | 2 | 2.2 | 22.3196 | 2397339.5875 | 13823.0077 | 2764601.5352 | 170000 | 41953442.7818 | 840 | 1680000
214 | 915.724 | 2 | 2.2 | 22.4235 | 2408388.846 | 13823.0077 | 2764601.5352 | 170000 | 42146804.8051 | 840 | 1680000
216 | 915.73 | 2 | 2.2 | 22.3833 | 2404112.0654 | 13823.0077 | 2764601.5352 | 170000 | 42071961.1443 | 840 | 1680000
218 | 915.584 | 2 | 2.2 | 22.3542 | 2401020.0827 | 13823.0077 | 2764601.5352 | 170000 | 42017851.4477 | 840 | 1680000
220 | 915.444 | 2 | 2.2 | 22.3247 | 2397881.2409 | 13823.0077 | 2764601.5352 | 170000 | 41962921.7163 | 840 | 1680000
222 | 913.52 | 2 | 2.2 | 22.426 | 2408649.8198 | 13823.0077 | 2764601.5352 | 170000 | 42151371.8464 | 840 | 1680000
224 | 912.524 | 2 | 2.2 | 22.4592 | 2412183.879 | 13823.0077 | 2764601.5352 | 170000 | 42213217.8833 | 840 | 1680000
226 | 912.565 | 2 | 2.2 | 22.4164 | 2407634.4055 | 13823.0077 | 2764601.5352 | 170000 | 42133602.0966 | 840 | 1680000
228 | 913.484 | 2 | 2.2 | 22.3092 | 2396240.0161 | 13823.0077 | 2764601.5352 | 170000 | 41934200.2814 | 840 | 1680000
230 | 913.545 | 2 | 2.2 | 22.265 | 2391533.9818 | 13823.0077 | 2764601.5352 | 170000 | 41851844.6823 | 840 | 1680000
232 | 914.546 | 2 | 2.2 | 22.1518 | 2379498.6226 | 13823.0077 | 2764601.5352 | 170000 | 41641225.895 | 840 | 1680000
234 | 918.285 | 2 | 2.2 | 21.8378 | 2346109.0406 | 13823.0077 | 2764601.5352 | 170000 | 41056908.2096 | 840 | 1680000
236 | 919.357 | 2 | 2.2 | 21.7194 | 2333515.0892 | 13823.0077 | 2764601.5352 | 170000 | 40836514.0614 | 840 | 1680000
238 | 918.649 | 2 | 2.2 | 21.7315 | 2334805.0193 | 13823.0077 | 2764601.5352 | 170000 | 40859087.8377 | 840 | 1680000
240 | 922.974 | 2 | 2.2 | 21.3745 | 2296830.0585 | 13823.0077 | 2764601.5352 | 170000 | 40194526.0235 | 840 | 1680000
242 | 927.375 | 2 | 2.2 | 21.012 | 2258249.316 | 13823.0077 | 2764601.5352 | 170000 | 39519363.0308 | 840 | 1680000
244 | 929.253 | 2 | 2.2 | 20.8345 | 2239353.6697 | 13823.0077 | 2764601.5352 | 170000 | 39188689.2192 | 840 | 1680000
246 | 930.863 | 2 | 2.2 | 20.6766 | 2222547.4429 | 13823.0077 | 2764601.5352 | 170000 | 38894580.25 | 840 | 1680000
248 | 931.924 | 2 | 2.2 | 20.559 | 2210025.825 | 13823.0077 | 2764601.5352 | 170000 | 38675451.937 | 840 | 1680000
250 | 936.722 | 2 | 2.2 | 20.1674 | 2168314.7733 | 13823.0077 | 2764601.5352 | 170000 | 37945508.5336 | 840 | 1680000
252 | 941.777 | 2 | 2.2 | 19.7569 | 2124580.276 | 13823.0077 | 2764601.5352 | 170000 | 37180154.8292 | 840 | 1680000
254 | 948.143 | 2 | 2.2 | 19.2503 | 2070579.9683 | 13823.0077 | 2764601.5352 | 170000 | 36235149.4444 | 840 | 1680000
256 | 955.417 | 2 | 2.2 | 18.677 | 2009451.8796 | 13823.0077 | 2764601.5352 | 170000 | 35165407.8926 | 840 | 1680000
258 | 962.7 | 2 | 2.2 | 18.1032 | 1948220.9394 | 13823.0077 | 2764601.5352 | 170000 | 34093866.4392 | 840 | 1680000
260 | 969.281 | 2 | 2.2 | 17.5808 | 1892454.4879 | 13823.0077 | 2764601.5352 | 170000 | 33117953.5388 | 840 | 1680000
262 | 980.284 | 2 | 2.2 | 16.7341 | 1802013.7873 | 13823.0077 | 2764601.5352 | 170000 | 31535241.277 | 840 | 1680000
264 | 986.551 | 2 | 2.2 | 16.2347 | 1748638.5704 | 13823.0077 | 2764601.5352 | 170000 | 30601174.982 | 840 | 1680000
266 | 989.198 | 2 | 2.2 | 16.0008 | 1723629.1631 | 13823.0077 | 2764601.5352 | 170000 | 30163510.3536 | 840 | 1680000
268 | 994.39 | 2 | 2.2 | 15.5803 | 1678651.2223 | 13823.0077 | 2764601.5352 | 170000 | 29376396.3898 | 840 | 1680000
270 | 999.917 | 2 | 2.2 | 15.1352 | 1631026.8 | 13823.0077 | 2764601.5352 | 170000 | 28542968.9994 | 840 | 1680000
272 | 1004.623 | 2 | 2.2 | 14.7503 | 1589828.4709 | 13823.0077 | 2764601.5352 | 170000 | 27821998.2411 | 840 | 1680000
274 | 1008.819 | 2 | 2.2 | 14.4028 | 1552620.7565 | 13823.0077 | 2764601.5352 | 170000 | 27170863.2394 | 840 | 1680000
276 | 1007.834 | 2 | 2.2 | 14.4352 | 1556094.7463 | 13823.0077 | 2764601.5352 | 170000 | 27231658.0598 | 840 | 1680000
278 | 1005.626 | 2 | 2.2 | 14.5573 | 1569172.1918 | 13823.0077 | 2764601.5352 | 170000 | 27460513.3568 | 840 | 1680000
280 | 1001.623 | 2 | 2.2 | 14.8111 | 1596340.3105 | 13823.0077 | 2764601.5352 | 170000 | 27935955.434 | 840 | 1680000
282 | 1004.052 | 2 | 2.2 | 14.5932 | 1573009.7764 | 13823.0077 | 2764601.5352 | 170000 | 27527671.0878 | 840 | 1680000
284 | 1010.797 | 2 | 2.2 | 14.0587 | 1515774.111 | 13823.0077 | 2764601.5352 | 170000 | 26526046.942 | 840 | 1680000
286 | 1014.67 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
288 | 1017.319 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
290 | 1027.459 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
292 | 1031.99 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
294 | 1036.254 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
296 | 1040.127 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
298 | 1044.396 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
300 | 1051.339 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
302 | 1060.955 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
304 | 1070.227 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
306 | 1072.691 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
308 | 1076.503 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
310 | 1083.996 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
312 | 1097.188 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
314 | 1103.545 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
316 | 1105.174 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
318 | 1111.657 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
320 | 1122.935 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
322 | 1128.197 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
324 | 1132.561 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
326 | 1131.854 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
328 | 1133.338 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
330 | 1136.405 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
332 | 1128.709 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
334 | 1120.713 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
336 | 1115.226 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
338 | 1108.709 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
340 | 1102.499 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
342 | 1096.349 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
344 | 1090.39 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
346 | 1087.765 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
348 | 1084.661 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
350 | 1081.662 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
352 | 1076.872 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
354 | 1070.898 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
356 | 1065.018 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
358 | 1059.58 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
360 | 1055.284 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
362 | 1050.886 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
364 | 1052.647 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
366 | 1051.117 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
368 | 1048.266 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
370 | 1040.172 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
372 | 1033.483 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
374 | 1030.95 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
376 | 1032.263 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
378 | 1031.391 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
380 | 1025.791 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
382 | 1020.911 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
384 | 1015.65 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
386 | 1012.139 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
388 | 1010.472 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
390 | 1005.401 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
392 | 996.666 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
394 | 991.35 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
396 | 990.486 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
398 | 992.761 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
400 | 999.077 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
402 | 1001.8 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
404 | 1002.224 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
406 | 1002.003 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
408 | 1003.596 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
410 | 994.111 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
412 | 983.925 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
414 | 972.347 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
416 | 963.901 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
418 | 963.258 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
420 | 965.872 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
422 | 966.177 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
424 | 973.825 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
426 | 983.972 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
428 | 994.096 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
430 | 991.695 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
432 | 984.933 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
434 | 974.509 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
436 | 966.698 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
438 | 963.618 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
440 | 957.803 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
442 | 954.277 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
444 | 947.182 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
446 | 938.045 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
448 | 930.871 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
450 | 926.391 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
452 | 918.344 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
454 | 911.505 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
456 | 903.61 | 2 | 1.8 | 11.4165 | 1007142.3563 | 11309.7336 | 2261946.7106 | 170000 | 17624991.2354 | 660 | 1320000
458 | 900.63 | 2 | 1.8 | 11.5046 | 1014869.4951 | 11309.7336 | 2261946.7106 | 170000 | 17760216.1637 | 660 | 1320000
460 | 904.066 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
462 | 915.092 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
464 | 905.556 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
466 | 905.271 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
468 | 901.918 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
470 | 895.651 | 2 | 1.8 | 11.2595 | 993383.3975 | 11309.7336 | 2261946.7106 | 170000 | 17384209.4562 | 660 | 1320000
472 | 892.304 | 2 | 1.8 | 11.3697 | 1003042.1946 | 11309.7336 | 2261946.7106 | 170000 | 17553238.4059 | 660 | 1320000
474 | 895.279 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
476 | 896.818 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
478 | 909.921 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
480 | 926.295 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
482 | 924.888 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
484 | 919.044 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
486 | 911.164 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
488 | 903.893 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
490 | 901.953 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
492 | 900.198 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
494 | 904.177 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
496 | 912.253 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
498 | 915.297 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
500 | 919.629 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000

## Pipeline Instalation Costs
Option 1B Excavation and Back Fill Pricing
Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Trench Width (m) | Trench Depth (m) | Excavation (m3) | Bedding and Cradle Fill (m3) | Main fill (m3) | Spoil (m3) | Excavation Cost | Bedding and Cradle Fill Cost | Main Fill Cost | Spoil Cost
2 | 1069.018 | 0 | 2.2 | 3.2 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1067.321 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
6 | 1064.035 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
8 | 1063.832 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
10 | 1067.893 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
12 | 1075.133 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
14 | 1082.768 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
16 | 1089.726 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
18 | 1094.131 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
20 | 1097.897 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
22 | 1101.67 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
24 | 1095.952 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
26 | 1090.107 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
28 | 1085.781 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
30 | 1081.89 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
32 | 1077.937 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
34 | 1074.89 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
36 | 1071.114 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
38 | 1065.311 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
40 | 1059.051 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
42 | 1054.28 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
44 | 1053.871 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
46 | 1050.42 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
48 | 1052.704 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
50 | 1056.355 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
52 | 1058.466 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
54 | 1055.99 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
56 | 1055.66 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
58 | 1056.404 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
60 | 1056.841 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
62 | 1056.377 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
64 | 1052.503 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
66 | 1046.022 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
68 | 1036.575 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
70 | 1031.818 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
72 | 1027.675 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
74 | 1023.844 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
76 | 1020.888 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
78 | 1023.648 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
80 | 1027.566 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
82 | 1032.371 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
84 | 1034.983 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
86 | 1033.213 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
88 | 1031.188 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
90 | 1029.08 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
92 | 1026.322 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
94 | 1023.207 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
96 | 1021.503 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
98 | 1019.765 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
100 | 1018.493 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
102 | 1016.444 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
104 | 1013.288 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
106 | 1007.843 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
108 | 1001.282 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
110 | 996.609 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
112 | 992.999 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
114 | 993.639 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
116 | 994.611 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
118 | 995.751 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
120 | 996.479 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
122 | 996.147 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
124 | 992.094 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
126 | 985.623 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
128 | 977.759 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
130 | 969.772 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
132 | 981.785 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
134 | 991.458 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
136 | 987.77 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
138 | 982.725 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
140 | 977.559 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
142 | 975.289 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
144 | 973.968 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
146 | 962.473 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
148 | 951.285 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
150 | 948.174 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
152 | 944.641 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
154 | 941.566 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
156 | 940.942 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
158 | 939.726 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
160 | 936.738 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
162 | 933.65 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
164 | 932.745 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
166 | 931.696 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
168 | 930.999 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
170 | 930.885 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
172 | 930.378 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
174 | 931.324 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
176 | 933.53 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
178 | 932.714 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
180 | 928.311 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
182 | 924.179 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
184 | 928.398 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
186 | 930.866 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
188 | 928.411 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
190 | 927.849 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
192 | 926.71 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
194 | 926.201 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
196 | 924.509 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
198 | 923.417 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
200 | 923.011 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
202 | 921.969 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
204 | 920.661 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
206 | 920.243 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
208 | 919.297 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
210 | 917.533 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
212 | 917.684 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
214 | 915.724 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
216 | 915.73 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
218 | 915.584 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
220 | 915.444 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
222 | 913.52 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
224 | 912.524 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
226 | 912.565 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
228 | 913.484 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
230 | 913.545 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
232 | 914.546 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
234 | 918.285 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
236 | 919.357 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
238 | 918.649 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
240 | 922.974 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
242 | 927.375 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
244 | 929.253 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
246 | 930.863 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
248 | 931.924 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
250 | 936.722 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
252 | 941.777 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
254 | 948.143 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
256 | 955.417 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
258 | 962.7 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
260 | 969.281 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
262 | 980.284 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
264 | 986.551 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
266 | 989.198 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
268 | 994.39 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
270 | 999.917 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
272 | 1004.623 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
274 | 1008.819 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
276 | 1007.834 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
278 | 1005.626 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
280 | 1001.623 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
282 | 1004.052 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
284 | 1010.797 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
286 | 1014.67 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
288 | 1017.319 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
290 | 1027.459 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
292 | 1031.99 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
294 | 1036.254 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
296 | 1040.127 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
298 | 1044.396 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
300 | 1051.339 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
302 | 1060.955 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
304 | 1070.227 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
306 | 1072.691 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
308 | 1076.503 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
310 | 1083.996 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
312 | 1097.188 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
314 | 1103.545 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
316 | 1105.174 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
318 | 1111.657 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
320 | 1122.935 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
322 | 1128.197 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
324 | 1132.561 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
326 | 1131.854 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
328 | 1133.338 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
330 | 1136.405 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
332 | 1128.709 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
334 | 1120.713 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
336 | 1115.226 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
338 | 1108.709 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
340 | 1102.499 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
342 | 1096.349 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
344 | 1090.39 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
346 | 1087.765 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
348 | 1084.661 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
350 | 1081.662 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
352 | 1076.872 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
354 | 1070.898 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
356 | 1065.018 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
358 | 1059.58 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
360 | 1055.284 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
362 | 1050.886 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
364 | 1052.647 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
366 | 1051.117 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
368 | 1048.266 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
370 | 1040.172 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
372 | 1033.483 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
374 | 1030.95 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
376 | 1032.263 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
378 | 1031.391 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
380 | 1025.791 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
382 | 1020.911 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
384 | 1015.65 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
386 | 1012.139 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
388 | 1010.472 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
390 | 1005.401 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
392 | 996.666 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
394 | 991.35 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
396 | 990.486 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
398 | 992.761 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
400 | 999.077 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
402 | 1001.8 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
404 | 1002.224 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
406 | 1002.003 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
408 | 1003.596 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
410 | 994.111 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
412 | 983.925 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
414 | 972.347 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
416 | 963.901 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
418 | 963.258 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
420 | 965.872 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
422 | 966.177 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
424 | 973.825 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
426 | 983.972 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
428 | 994.096 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
430 | 991.695 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
432 | 984.933 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
434 | 974.509 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
436 | 966.698 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
438 | 963.618 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
440 | 957.803 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
442 | 954.277 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
444 | 947.182 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
446 | 938.045 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
448 | 930.871 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
450 | 926.391 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
452 | 918.344 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
454 | 911.505 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
456 | 903.61 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
458 | 900.63 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
460 | 904.066 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
462 | 915.092 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
464 | 905.556 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
466 | 905.271 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
468 | 901.918 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
470 | 895.651 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
472 | 892.304 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
474 | 895.279 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
476 | 896.818 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
478 | 909.921 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
480 | 926.295 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
482 | 924.888 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
484 | 919.044 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
486 | 911.164 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
488 | 903.893 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
490 | 901.953 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
492 | 900.198 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
494 | 904.177 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
496 | 912.253 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
498 | 915.297 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
500 | 919.629 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281

## Capital Costs
Option 1B Capital Costs
Pipe Cost | 7600430164.3155
Pipe Laying and Joining | 1520086032.8631
Pipe Trench Excavation & Back Fill | 877383586.8403
Air Valve, Scour Valve & Isolating Cost | 385760000
Pump Station Cost PS 1 | 83848876.482
Option 1B Capital Costs (Pula)
Pipe Cost | 6909481967.5595
Pipe Laying and Joining | 1381896393.5119
Pipe Trench Excavation & Back Fill | 797621442.582
Air Valve, Scour Valve & Isolating Cost | 350690909.0909
Pump Station Cost PS 1 | 76226251.3473

## Maintenance Costs
Option 1B Maintenance Costs
Item | Percentage Per Annum | Cost R/year
Civil | 0.5% | 38002150.8216
Mechanical & Electrical | 4% | 18784355.0593
Total |  | 56786505.8809
Option 1B Maintenance Costs (Pula)
Item | Percentage Per Annum | Cost P/year
Civil | 0.5% | 34547409.8378
Mechanical & Electrical | 4% | 17076686.4175
Total |  | 51624096.2553

## Pumping Costs Calculation
Option 1B Pumping Costs Calculations
Pipeline Details |  |  |  | New Pipe Flow Equation |  |  | Average Pipe Flow Equation |  |  | Old Pipe Flow Equation |  |  | Biofilm Pipe Flow Equation
Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component
2 | 1069.018 | 0 | 2.2 | 0.008468 | 0 | 0 | 0.0094904 | 0 | 0 | 0.011153 | 0 | 0 | 0.014105 | 0 | 0
4 | 1067.321 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
6 | 1064.035 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
8 | 1063.832 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
10 | 1067.893 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
12 | 1075.133 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
14 | 1082.768 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
16 | 1089.726 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
18 | 1094.131 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
20 | 1097.897 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
22 | 1101.67 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
24 | 1095.952 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
26 | 1090.107 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
28 | 1085.781 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
30 | 1081.89 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
32 | 1077.937 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
34 | 1074.89 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
36 | 1071.114 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
38 | 1065.311 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
40 | 1059.051 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
42 | 1054.28 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
44 | 1053.871 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
46 | 1050.42 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
48 | 1052.704 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
50 | 1056.355 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
52 | 1058.466 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
54 | 1055.99 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
56 | 1055.66 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
58 | 1056.404 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
60 | 1056.841 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
62 | 1056.377 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
64 | 1052.503 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
66 | 1046.022 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
68 | 1036.575 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
70 | 1031.818 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
72 | 1027.675 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
74 | 1023.844 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
76 | 1020.888 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
78 | 1023.648 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
80 | 1027.566 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
82 | 1032.371 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
84 | 1034.983 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
86 | 1033.213 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
88 | 1031.188 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
90 | 1029.08 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
92 | 1026.322 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
94 | 1023.207 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
96 | 1021.503 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
98 | 1019.765 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
100 | 1018.493 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
102 | 1016.444 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
104 | 1013.288 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
106 | 1007.843 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
108 | 1001.282 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
110 | 996.609 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
112 | 992.999 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
114 | 993.639 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
116 | 994.611 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
118 | 995.751 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
120 | 996.479 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
122 | 996.147 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
124 | 992.094 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
126 | 985.623 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
128 | 977.759 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
130 | 969.772 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
132 | 981.785 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
134 | 991.458 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
136 | 987.77 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
138 | 982.725 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
140 | 977.559 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
142 | 975.289 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
144 | 973.968 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
146 | 962.473 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
148 | 951.285 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
150 | 948.174 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
152 | 944.641 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
154 | 941.566 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
156 | 940.942 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
158 | 939.726 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
160 | 936.738 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
162 | 933.65 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
164 | 932.745 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
166 | 931.696 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
168 | 930.999 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
170 | 930.885 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
172 | 930.378 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
174 | 931.324 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
176 | 933.53 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
178 | 932.714 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
180 | 928.311 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
182 | 924.179 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
184 | 928.398 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
186 | 930.866 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
188 | 928.411 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
190 | 927.849 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
192 | 926.71 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
194 | 926.201 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
196 | 924.509 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
198 | 923.417 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
200 | 923.011 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
202 | 921.969 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
204 | 920.661 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
206 | 920.243 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
208 | 919.297 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
210 | 917.533 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
212 | 917.684 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
214 | 915.724 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
216 | 915.73 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
218 | 915.584 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
220 | 915.444 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
222 | 913.52 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
224 | 912.524 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
226 | 912.565 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
228 | 913.484 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
230 | 913.545 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
232 | 914.546 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
234 | 918.285 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
236 | 919.357 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
238 | 918.649 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
240 | 922.974 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
242 | 927.375 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
244 | 929.253 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
246 | 930.863 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
248 | 931.924 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
250 | 936.722 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
252 | 941.777 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
254 | 948.143 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
256 | 955.417 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
258 | 962.7 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
260 | 969.281 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
262 | 980.284 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
264 | 986.551 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
266 | 989.198 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
268 | 994.39 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
270 | 999.917 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
272 | 1004.623 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
274 | 1008.819 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
276 | 1007.834 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
278 | 1005.626 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
280 | 1001.623 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
282 | 1004.052 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
284 | 1010.797 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
286 | 1014.67 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
288 | 1017.319 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
290 | 1027.459 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
292 | 1031.99 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
294 | 1036.254 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
296 | 1040.127 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
298 | 1044.396 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
300 | 1051.339 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
302 | 1060.955 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
304 | 1070.227 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
306 | 1072.691 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
308 | 1076.503 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
310 | 1083.996 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
312 | 1097.188 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
314 | 1103.545 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
316 | 1105.174 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
318 | 1111.657 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
320 | 1122.935 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
322 | 1128.197 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
324 | 1132.561 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
326 | 1131.854 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
328 | 1133.338 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
330 | 1136.405 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
332 | 1128.709 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
334 | 1120.713 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
336 | 1115.226 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
338 | 1108.709 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
340 | 1102.499 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
342 | 1096.349 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
344 | 1090.39 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
346 | 1087.765 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
348 | 1084.661 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
350 | 1081.662 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
352 | 1076.872 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
354 | 1070.898 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
356 | 1065.018 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
358 | 1059.58 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
360 | 1055.284 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
362 | 1050.886 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
364 | 1052.647 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
366 | 1051.117 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
368 | 1048.266 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
370 | 1040.172 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
372 | 1033.483 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
374 | 1030.95 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
376 | 1032.263 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
378 | 1031.391 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
380 | 1025.791 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
382 | 1020.911 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
384 | 1015.65 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
386 | 1012.139 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
388 | 1010.472 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
390 | 1005.401 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
392 | 996.666 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
394 | 991.35 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
396 | 990.486 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
398 | 992.761 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
400 | 999.077 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
402 | 1001.8 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
404 | 1002.224 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
406 | 1002.003 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
408 | 1003.596 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
410 | 994.111 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
412 | 983.925 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
414 | 972.347 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
416 | 963.901 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
418 | 963.258 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
420 | 965.872 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
422 | 966.177 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
424 | 973.825 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
426 | 983.972 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
428 | 994.096 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
430 | 991.695 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
432 | 984.933 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
434 | 974.509 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
436 | 966.698 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
438 | 963.618 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
440 | 957.803 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
442 | 954.277 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
444 | 947.182 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
446 | 938.045 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
448 | 930.871 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
450 | 926.391 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
452 | 918.344 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
454 | 911.505 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
456 | 903.61 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
458 | 900.63 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
460 | 904.066 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
462 | 915.092 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
464 | 905.556 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
466 | 905.271 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
468 | 901.918 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
470 | 895.651 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
472 | 892.304 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
474 | 895.279 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
476 | 896.818 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
478 | 909.921 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
480 | 926.295 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
482 | 924.888 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
484 | 919.044 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
486 | 911.164 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
488 | 903.893 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
490 | 901.953 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
492 | 900.198 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
494 | 904.177 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
496 | 912.253 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
498 | 915.297 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
500 | 919.629 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928

## Pumping Costs
Option 1B Pumping Costs
PS 1
New Pipe - Year 4 to 18 |  | Average Pipe - Year 19 to 33 |  | Old Pipe - Year 34 to 48 |  | Biofilmed Pipe - Year 49 to 63
Pumping Head (m) | 200 | Pumping Head (m) | 200 | Pumping Head (m) | 200 | Pumping Head (m) | 200
Gravitational Head (m) | 149.389 | Gravitational Head (m) | 149.389 | Gravitational Head (m) | 149.389 | Gravitational Head (m) | 149.389
Flow Rate (m3/s) | 5.1838 | Flow Rate (m3/s) | 4.9094 | Flow Rate (m3/s) | 4.5426 | Flow Rate (m3/s) | 4.0521
Pumping Hours per Day | 24 | Pumping Hours per Day | 24 | Pumping Hours per Day | 24 | Pumping Hours per Day | 24
Peak Design Flow (m3/s) | 4.083 | Peak Design Flow | 4.083 | Peak Design Flow | 4.083 | Peak Design Flow | 4.083
Required Pumping Hours | 18.9 | Required Pumping Hours | 20 | Required Pumping Hours | 21.6 | Required Pumping Hours | 24
Pumpstation Power (kW) | 9367 | Pumpstation Power (kW) | 9367 | Pumpstation Power (kW) | 9367 | Pumpstation Power (kW) | 9367
Pumping Days per Year | 347 | Pumping Days per Year | 347 | Pumping Days per Year | 347 | Pumping Days per Year | 347
Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699
Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388
Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056
Energy Cost Per Year | 27678964.3268 | Energy Cost Per Year | 29289889.2968 | Energy Cost Per Year | 31633052.8895 | Energy Cost Per Year | 35147798.2786
Pipe Type | Energy Cost Per Year
New Pipe | 27678964.3268
Average Pipe | 29289889.2968
Old Pipe | 31633052.8895
Biofilm Pipe | 35147798.2786
Pipe Type | Energy Cost Per Year(Pula)
New Pipe | 25162694.8426
Average Pipe | 26627172.088
Old Pipe | 28757320.8086
Biofilm Pipe | 31952543.8896

## Life Cycle Costing (Pula)
Table 13: Option 1B Life Cycle Costing (Pula)
Year | Reference Year | Capital Cost | Electricity - Pumping Cost | Maintenance Cost | NPV at 6% Discount Rate | NPV at 8% Discount Rate | NPV at 10% Discount Rate
2010 | 0 | 2378979241.0229 |  |  | 2378979241.0229 | 2378979241.0229 | 2378979241.0229
2011 | 1 | 2378979241.0229 |  |  | 2378979241.0229 | 2378979241.0229 | 2378979241.0229
2012 | 2 | 2378979241.0229 |  |  | 2378979241.0229 | 2378979241.0229 | 2378979241.0229
2013 | 3 | 2378979241.0229 |  |  | 2378979241.0229 | 2378979241.0229 | 2378979241.0229
2014 | 4 | 0 | 25162694.8426 | 51624096.2553 | 60822330.649 | 56440583.7574 | 52446411.5142
2015 | 5 | 0 | 25162694.8426 | 51624096.2553 | 57379557.2161 | 52259799.7754 | 47678555.922
2016 | 6 | 0 | 25162694.8426 | 51624096.2553 | 54131657.751 | 48388703.4957 | 43344141.7472
2017 | 7 | 0 | 25162694.8426 | 51624096.2553 | 51067601.6519 | 44804355.0886 | 39403765.2248
2018 | 8 | 0 | 25162694.8426 | 51624096.2553 | 48176982.6905 | 41485513.9709 | 35821604.7498
2019 | 9 | 0 | 25162694.8426 | 51624096.2553 | 45449983.6702 | 38412512.9361 | 32565095.2271
2020 | 10 | 0 | 25162694.8426 | 51624096.2553 | 42877343.0851 | 35567141.6075 | 29604632.0246
2021 | 11 | 0 | 25162694.8426 | 51624096.2553 | 40450323.6652 | 32932538.5254 | 26913301.8406
2022 | 12 | 0 | 25162694.8426 | 51624096.2553 | 38160682.703 | 30493091.2272 | 24466638.0369
2023 | 13 | 0 | 25162694.8426 | 51624096.2553 | 36000644.0595 | 28234343.7289 | 22242398.2153
2024 | 14 | 0 | 25162694.8426 | 51624096.2553 | 33962871.7542 | 26142910.8601 | 20220362.0139
2025 | 15 | 0 | 25162694.8426 | 51624096.2553 | 32040445.0511 | 24206398.9446 | 18382147.2854
2026 | 16 | 0 | 25162694.8426 | 51624096.2553 | 30226834.9539 | 22413332.3561 | 16711042.9867
2027 | 17 | 0 | 25162694.8426 | 51624096.2553 | 28515882.032 | 20753085.5149 | 15191857.2607
2028 | 18 | 0 | 25162694.8426 | 51624096.2553 | 26901775.5019 | 19215819.9212 | 13810779.3279
2029 | 19 | 0 | 26627172.088 | 51624096.2553 | 25863062.2755 | 18131762.8982 | 12794707.6664
2030 | 20 | 0 | 26627172.088 | 51624096.2553 | 24399115.3543 | 16788669.3502 | 11631552.424
2031 | 21 | 0 | 26627172.088 | 51624096.2553 | 23018033.3531 | 15545064.2131 | 10574138.5673
2032 | 22 | 0 | 26627172.088 | 51624096.2553 | 21715125.8048 | 14393577.9751 | 9612853.243
2033 | 23 | 0 | 26627172.088 | 51624096.2553 | 20485967.7404 | 13327387.014 | 8738957.4936
2034 | 24 | 0 | 26627172.088 | 51624096.2553 | 19326384.6607 | 12340173.1611 | 7944506.8124
2035 | 25 | 0 | 26627172.088 | 51624096.2553 | 18232438.3592 | 11426086.2603 | 7222278.9204
2036 | 26 | 0 | 26627172.088 | 51624096.2553 | 17200413.5464 | 10579709.5003 | 6565708.1094
2037 | 27 | 0 | 26627172.088 | 51624096.2553 | 16226805.2325 | 9796027.315 | 5968825.554
2038 | 28 | 0 | 26627172.088 | 51624096.2553 | 15308306.8231 | 9070395.6621 | 5426205.0491
2039 | 29 | 0 | 26627172.088 | 51624096.2553 | 14441798.8897 | 8398514.5019 | 4932913.681
2040 | 30 | 0 | 26627172.088 | 51624096.2553 | 13624338.5752 | 7776402.3166 | 4484466.9827
2041 | 31 | 0 | 26627172.088 | 51624096.2553 | 12853149.5992 | 7200372.5154 | 4076788.1661
2042 | 32 | 0 | 26627172.088 | 51624096.2553 | 12125612.8295 | 6667011.5883 | 3706171.0601
2043 | 33 | 0 | 26627172.088 | 51624096.2553 | 11439257.3863 | 6173158.8781 | 3369246.4183
2044 | 34 | 0 | 28757320.8086 | 51624096.2553 | 11085524.3234 | 5871485.2154 | 3146330.6634
2045 | 35 | 0 | 28757320.8086 | 51624096.2553 | 10458041.8145 | 5436560.3847 | 2860300.6031
2046 | 36 | 0 | 28757320.8086 | 51624096.2553 | 9866077.1835 | 5033852.208 | 2600273.2755
2047 | 37 | 0 | 28757320.8086 | 51624096.2553 | 9307619.9844 | 4660974.2667 | 2363884.7959
2048 | 38 | 0 | 28757320.8086 | 51624096.2553 | 8780773.5702 | 4315716.9136 | 2148986.1781
2049 | 39 | 0 | 28757320.8086 | 51624096.2553 | 8283748.6512 | 3996034.1793 | 1953623.7983
2050 | 40 | 0 | 28757320.8086 | 51624096.2553 | 7814857.2181 | 3700031.6475 | 1776021.6348
2051 | 41 | 0 | 28757320.8086 | 51624096.2553 | 7372506.8095 | 3425955.2291 | 1614565.1225
2052 | 42 | 0 | 28757320.8086 | 51624096.2553 | 6955195.1033 | 3172180.7677 | 1467786.475
2053 | 43 | 0 | 28757320.8086 | 51624096.2553 | 6561504.8144 | 2937204.4145 | 1334351.3409
2054 | 44 | 0 | 28757320.8086 | 51624096.2553 | 6190098.8815 | 2719633.7172 | 1213046.6736
2055 | 45 | 0 | 28757320.8086 | 51624096.2553 | 5839715.926 | 2518179.3678 | 1102769.7033
2056 | 46 | 0 | 28757320.8086 | 51624096.2553 | 5509165.9679 | 2331647.5627 | 1002517.9121
2057 | 47 | 0 | 28757320.8086 | 51624096.2553 | 5197326.3848 | 2158932.9285 | 911379.9201
2058 | 48 | 0 | 28757320.8086 | 51624096.2553 | 4903138.0989 | 1999011.9708 | 828527.2
2059 | 49 | 0 | 31952543.8896 | 51624096.2553 | 4809473.2124 | 1924513.1781 | 783147.0843
2060 | 50 | 0 | 31952543.8896 | 51624096.2553 | 4537238.8796 | 1781956.6464 | 711951.8948
2061 | 51 | 0 | 31952543.8896 | 51624096.2553 | 4280414.0374 | 1649959.8578 | 647228.9953
2062 | 52 | 0 | 31952543.8896 | 51624096.2553 | 4038126.4503 | 1527740.6091 | 588389.9957
2063 | 53 | 0 | 31952543.8896 | 51624096.2553 | 3809553.255 | 1414574.638 | 534899.9961
2064 | 54 | 0 | 31952543.8896 | 51624096.2553 | 3593918.1651 | 1309791.3315 | 486272.7238
2065 | 55 | 0 | 31952543.8896 | 51624096.2553 | 3390488.835 | 1212769.7514 | 442066.1125
2066 | 56 | 0 | 31952543.8896 | 51624096.2553 | 3198574.3727 | 1122934.955 | 401878.2841
2067 | 57 | 0 | 31952543.8896 | 51624096.2553 | 3017522.9931 | 1039754.5879 | 365343.8946
2068 | 58 | 0 | 31952543.8896 | 51624096.2553 | 2846719.8048 | 962735.7296 | 332130.8133
2069 | 59 | 0 | 31952543.8896 | 51624096.2553 | 2685584.7215 | 891421.9718 | 301937.103
2070 | 60 | 0 | 31952543.8896 | 51624096.2553 | 2533570.492 | 825390.7147 | 274488.2755
2071 | 61 | 0 | 31952543.8896 | 51624096.2553 | 2390160.8415 | 764250.6617 | 249534.7959
2072 | 62 | 0 | 31952543.8896 | 51624096.2553 | 2254868.7184 | 707639.5016 | 226849.8144
2073 | 63 | 0 | 31952543.8896 | 51624096.2553 | 2127234.64 | 655221.7607 | 206227.104
[5 empty] | 10571980435.1066 | 10277349465.6198 | 10094645729.8007

## Life Cycle Costing
Table 13: Option 1B Life Cycle Costing
Year | Reference Year | Capital Cost | Electricity - Pumping Cost | Maintenance Cost | NPV at 6% Discount Rate | NPV at 8% Discount Rate | NPV at 10% Discount Rate
2010 | 0 | 2616877165.1252 |  |  | 2616877165.1252 | 2616877165.1252 | 2616877165.1252
2011 | 1 | 2616877165.1252 |  |  | 2616877165.1252 | 2616877165.1252 | 2616877165.1252
2012 | 2 | 2616877165.1252 |  |  | 2616877165.1252 | 2616877165.1252 | 2616877165.1252
2013 | 3 | 2616877165.1252 |  |  | 2616877165.1252 | 2616877165.1252 | 2616877165.1252
2014 | 4 | 0 | 27678964.3268 | 56786505.8809 | 66904563.7139 | 62084642.1331 | 57691052.6656
2015 | 5 | 0 | 27678964.3268 | 56786505.8809 | 63117512.9377 | 57485779.7529 | 52446411.5142
2016 | 6 | 0 | 27678964.3268 | 56786505.8809 | 59544823.5261 | 53227573.8453 | 47678555.922
2017 | 7 | 0 | 27678964.3268 | 56786505.8809 | 56174361.8171 | 49284790.5975 | 43344141.7472
2018 | 8 | 0 | 27678964.3268 | 56786505.8809 | 52994680.9595 | 45634065.368 | 39403765.2248
2019 | 9 | 0 | 27678964.3268 | 56786505.8809 | 49994982.0373 | 42253764.2297 | 35821604.7498
2020 | 10 | 0 | 27678964.3268 | 56786505.8809 | 47165077.3936 | 39123855.7682 | 32565095.2271
2021 | 11 | 0 | 27678964.3268 | 56786505.8809 | 44495356.0317 | 36225792.378 | 29604632.0246
2022 | 12 | 0 | 27678964.3268 | 56786505.8809 | 41976750.9733 | 33542400.35 | 26913301.8406
2023 | 13 | 0 | 27678964.3268 | 56786505.8809 | 39600708.4654 | 31057778.1018 | 24466638.0369
2024 | 14 | 0 | 27678964.3268 | 56786505.8809 | 37359158.9296 | 28757201.9461 | 22242398.2153
2025 | 15 | 0 | 27678964.3268 | 56786505.8809 | 35244489.5563 | 26627038.839 | 20220362.0139
2026 | 16 | 0 | 27678964.3268 | 56786505.8809 | 33249518.4493 | 24654665.5917 | 18382147.2854
2027 | 17 | 0 | 27678964.3268 | 56786505.8809 | 31367470.2352 | 22828394.0664 | 16711042.9867
2028 | 18 | 0 | 27678964.3268 | 56786505.8809 | 29591953.0521 | 21137401.9133 | 15191857.2607
2029 | 19 | 0 | 29289889.2968 | 56786505.8809 | 28449368.5031 | 19944939.188 | 14074178.4331
2030 | 20 | 0 | 29289889.2968 | 56786505.8809 | 26839026.8897 | 18467536.2852 | 12794707.6664
2031 | 21 | 0 | 29289889.2968 | 56786505.8809 | 25319836.6884 | 17099570.6344 | 11631552.424
2032 | 22 | 0 | 29289889.2968 | 56786505.8809 | 23886638.3853 | 15832935.7726 | 10574138.5673
2033 | 23 | 0 | 29289889.2968 | 56786505.8809 | 22534564.5144 | 14660125.7154 | 9612853.243
2034 | 24 | 0 | 29289889.2968 | 56786505.8809 | 21259023.1268 | 13574190.4772 | 8738957.4936
2035 | 25 | 0 | 29289889.2968 | 56786505.8809 | 20055682.1951 | 12568694.8863 | 7944506.8124
2036 | 26 | 0 | 29289889.2968 | 56786505.8809 | 18920454.901 | 11637680.4503 | 7222278.9204
2037 | 27 | 0 | 29289889.2968 | 56786505.8809 | 17849485.7557 | 10775630.0466 | 6565708.1094
2038 | 28 | 0 | 29289889.2968 | 56786505.8809 | 16839137.5054 | 9977435.2283 | 5968825.554
2039 | 29 | 0 | 29289889.2968 | 56786505.8809 | 15885978.7787 | 9238365.9521 | 5426205.0491
2040 | 30 | 0 | 29289889.2968 | 56786505.8809 | 14986772.4327 | 8554042.5483 | 4932913.681
2041 | 31 | 0 | 29289889.2968 | 56786505.8809 | 14138464.5591 | 7920409.7669 | 4484466.9827
2042 | 32 | 0 | 29289889.2968 | 56786505.8809 | 13338174.1124 | 7333712.7471 | 4076788.1661
2043 | 33 | 0 | 29289889.2968 | 56786505.8809 | 12583183.1249 | 6790474.7659 | 3706171.0601
2044 | 34 | 0 | 31633052.8895 | 56786505.8809 | 12194076.7557 | 6458633.737 | 3460963.7297
2045 | 35 | 0 | 31633052.8895 | 56786505.8809 | 11503845.996 | 5980216.4231 | 3146330.6634
2046 | 36 | 0 | 31633052.8895 | 56786505.8809 | 10852684.9019 | 5537237.4288 | 2860300.6031
2047 | 37 | 0 | 31633052.8895 | 56786505.8809 | 10238381.9829 | 5127071.6933 | 2600273.2755
2048 | 38 | 0 | 31633052.8895 | 56786505.8809 | 9658850.9272 | 4747288.6049 | 2363884.7959
2049 | 39 | 0 | 31633052.8895 | 56786505.8809 | 9112123.5163 | 4395637.5972 | 2148986.1781
2050 | 40 | 0 | 31633052.8895 | 56786505.8809 | 8596342.9399 | 4070034.8122 | 1953623.7983
2051 | 41 | 0 | 31633052.8895 | 56786505.8809 | 8109757.4904 | 3768550.752 | 1776021.6348
2052 | 42 | 0 | 31633052.8895 | 56786505.8809 | 7650714.6136 | 3489398.8445 | 1614565.1225
2053 | 43 | 0 | 31633052.8895 | 56786505.8809 | 7217655.2959 | 3230924.856 | 1467786.475
2054 | 44 | 0 | 31633052.8895 | 56786505.8809 | 6809108.7697 | 2991597.0889 | 1334351.3409
2055 | 45 | 0 | 31633052.8895 | 56786505.8809 | 6423687.5186 | 2769997.3045 | 1213046.6736
2056 | 46 | 0 | 31633052.8895 | 56786505.8809 | 6060082.5647 | 2564812.319 | 1102769.7033
2057 | 47 | 0 | 31633052.8895 | 56786505.8809 | 5717059.0233 | 2374826.2213 | 1002517.9121
2058 | 48 | 0 | 31633052.8895 | 56786505.8809 | 5393451.9088 | 2198913.1679 | 911379.9201
2059 | 49 | 0 | 35147798.2786 | 56786505.8809 | 5290420.5336 | 2116964.4959 | 861461.7928
2060 | 50 | 0 | 35147798.2786 | 56786505.8809 | 4990962.7676 | 1960152.311 | 783147.0843
2061 | 51 | 0 | 35147798.2786 | 56786505.8809 | 4708455.4411 | 1814955.8436 | 711951.8948
2062 | 52 | 0 | 35147798.2786 | 56786505.8809 | 4441939.0954 | 1680514.67 | 647228.9953
2063 | 53 | 0 | 35147798.2786 | 56786505.8809 | 4190508.5805 | 1556032.1018 | 588389.9957
2064 | 54 | 0 | 35147798.2786 | 56786505.8809 | 3953309.9817 | 1440770.4646 | 534899.9961
2065 | 55 | 0 | 35147798.2786 | 56786505.8809 | 3729537.7185 | 1334046.7265 | 486272.7238
2066 | 56 | 0 | 35147798.2786 | 56786505.8809 | 3518431.8099 | 1235228.4505 | 442066.1125
2067 | 57 | 0 | 35147798.2786 | 56786505.8809 | 3319275.2924 | 1143730.0467 | 401878.2841
2068 | 58 | 0 | 35147798.2786 | 56786505.8809 | 3131391.7853 | 1059009.3025 | 365343.8946
2069 | 59 | 0 | 35147798.2786 | 56786505.8809 | 2954143.1937 | 980564.169 | 332130.8133
2070 | 60 | 0 | 35147798.2786 | 56786505.8809 | 2786927.5412 | 907929.7861 | 301937.103
2071 | 61 | 0 | 35147798.2786 | 56786505.8809 | 2629176.9257 | 840675.7279 | 274488.2755
2072 | 62 | 0 | 35147798.2786 | 56786505.8809 | 2480355.5902 | 778403.4518 | 249534.7959
2073 | 63 | 0 | 35147798.2786 | 56786505.8809 | 2339958.104 | 720743.9368 | 226849.8144
[5 empty] | 11629178478.6173 | 11305084412.1818 | 11104110302.7808