## Summary
Option 2B Summary
Item | Name | Chainage | Value
Pipeline | P1 | 0-8 | 2.2 | m - Diameter
Pump Station | PS1 | 8 | 200 | m - Pumping Head
Pipeline | P2 | 8-330 | 1.2 | m - Diameter
Break Pressure | BPT2 | 330 | 10 | m - Elevation
Pipeline | P3 | 330-482 | 1.8 | m - Diameter
Pipeline | P4 | 482-500 | 1.5 | m - Diameter

## Profile data
Longitudinal profile data - Botswana pipeline
| OPTION 1: Pipeline goes through Serule before joining to BPT1 | OPTION2: Pipeline goes directly to BPT1
CHAINAGE (km0 | NGL (m) | NGL (m) |  | Botswana 1
2 | 1069.018 | 1069.018 | Start | Botswana 2
4 | 1067.321 | 1067.321
6 | 1064.035 | 1064.035
8 | 1063.832 | 1063.832
10 | 1067.893 | 1067.893
12 | 1075.133 | 1075.133
14 | 1082.768 | 1082.768
16 | 1089.726 | 1089.726
18 | 1094.131 | 1094.131
20 | 1097.897 | 1097.897
22 | 1101.67 | 1101.67
24 | 1095.952 | 1095.952
26 | 1090.107 | 1090.107
28 | 1085.781 | 1085.781
30 | 1081.89 | 1081.89
32 | 1077.937 | 1077.937
34 | 1074.89 | 1074.89
36 | 1071.114 | 1071.114
38 | 1065.311 | 1065.311
40 | 1059.051 | 1059.051
42 | 1054.28 | 1054.28
44 | 1053.871 | 1053.871
46 | 1050.42 | 1050.42
48 | 1052.704 | 1052.704
50 | 1056.355 | 1056.355
52 | 1058.466 | 1058.466
54 | 1055.99 | 1055.99
56 | 1055.66 | 1055.66
58 | 1056.404 | 1056.404
60 | 1056.841 | 1056.841
62 | 1056.377 | 1056.377
64 | 1052.503 | 1052.503
66 | 1046.022 | 1046.022
68 | 1036.575 | 1036.575
70 | 1031.818 | 1031.818
72 | 1027.675 | 1027.675
74 | 1023.844 | 1023.844
76 | 1020.888 | 1020.888
78 | 1023.648 | 1023.648
80 | 1027.566 | 1027.566
82 | 1032.371 | 1032.371
84 | 1034.983 | 1034.983
86 | 1033.213 | 1033.213
88 | 1031.188 | 1031.188
90 | 1029.08 | 1029.08
92 | 1026.322 | 1026.322
94 | 1023.207 | 1023.207
96 | 1021.503 | 1021.503
98 | 1019.765 | 1019.765
100 | 1018.493 | 1018.493
102 | 1016.444 | 1016.444
104 | 1013.288 | 1013.288
106 | 1007.843 | 1007.843
108 | 1001.282 | 1001.282
110 | 996.609 | 996.609
112 | 992.999 | 992.999
114 | 993.639 | 993.639
116 | 994.611 | 994.611
118 | 995.751 | 995.751
120 | 996.479 | 996.479
122 | 996.147 | 996.147
124 | 992.094 | 992.094
126 | 985.623 | 985.623
128 | 977.759 | 977.759
130 | 969.772 | 969.772
132 | 981.785 | 981.785
134 | 991.458 | 991.458
136 | 987.77 | 987.77
138 | 982.725 | 982.725
140 | 977.559 | 977.559
142 | 975.289 | 975.289
144 | 973.968 | 973.968
146 | 962.473 | 962.473
148 | 951.285 | 951.285
150 | 948.174 | 948.174
152 | 944.641 | 944.641
154 | 941.566 | 941.566
156 | 940.942 | 940.942
158 | 939.726 | 939.726
160 | 936.738 | 936.738
162 | 933.65 | 933.65
164 | 932.745 | 932.745
166 | 931.696 | 931.696
168 | 930.999 | 930.999
170 | 930.885 | 930.885
172 | 930.378 | 930.378
174 | 931.324 | 931.324
176 | 933.53 | 933.53
178 | 932.714 | 932.714
180 | 928.311 | 928.311
182 | 924.179 | 924.179
184 | 928.398 | 928.398
186 | 930.866 | 930.866
188 | 928.411 | 928.411
190 | 927.849 | 927.849
192 | 926.71 | 926.71
194 | 926.201 | 926.201
196 | 924.509 | 924.509
198 | 923.417 | 923.417
200 | 923.011 | 923.011
202 | 921.969 | 921.969
204 | 920.661 | 920.661
206 | 920.243 | 920.243
208 | 919.297 | 919.297
210 | 917.533 | 917.533
212 | 917.684 | 917.684
214 | 915.724 | 915.724
216 | 915.73 | 915.73
218 | 915.584 | 915.584
220 | 915.444 | 915.444
222 | 913.52 | 913.52
224 | 912.524 | 912.524
226 | 912.565 | 912.565
228 | 913.484 | 913.484
230 | 913.545 | 913.545
232 | 914.546 | 914.546
234 | 918.285 | 918.285
236 | 919.357 | 919.357
238 | 918.649 | 918.649
240 | 922.974 | 922.974
242 | 927.375 | 927.375
244 | 929.253 | 929.253
246 | 930.863 | 930.863
248 | 931.924 | 931.924
250 | 936.722 | 936.722
252 | 941.777 | 941.777
254 | 948.143 | 948.143
256 | 955.417 | 955.417
258 | 962.7 | 962.7
260 | 969.281 | 969.281
262 | 980.284 | 980.284
264 | 986.551 | 986.551
266 | 989.198 | 989.198
268 | 994.39 | 994.39
270 | 999.917 | 999.917
272 | 1004.623 | 1004.623
274 | 1008.819 | 1008.819
276 | 1007.834 | 1007.834
278 | 1005.626 | 1005.626
280 | 1001.623 | 1001.623
282 | 1004.052 | 1004.052
284 | 1010.797 | 1010.797
286 | 1014.67 | 1014.67
288 | 1017.319 | 1017.319
290 | 1027.459 | 1027.459
292 | 1031.99 | 1031.99
294 | 1036.254 | 1036.254
296 | 1040.127 | 1040.127
298 | 1044.396 | 1044.396
300 | 1051.339 | 1051.339
302 | 1060.955 | 1060.955
304 | 1070.227 | 1070.227
306 | 1072.691 | 1072.691
308 | 1076.503 | 1076.503
310 | 1083.996 | 1083.996
312 | 1097.188 | 1097.188
314 | 1103.545 | 1103.545
316 | 1105.174 | 1105.174
318 | 1111.657 | 1111.657
320 | 1122.935 | 1122.935
322 | 1128.197 | 1128.197
324 | 1132.561 | 1132.561
326 | 1131.854 | 1131.854
328 | 1133.338 | 1133.338
330 | 1136.405 | 1136.405
332 | 1128.709 | 1128.709
334 | 1120.713 | 1120.713
336 | 1115.226 | 1115.226
338 | 1108.709 | 1108.709
340 | 1102.499 | 1102.499
342 | 1096.349 | 1096.349
344 | 1090.39 | 1090.39
346 | 1087.765 | 1087.765
348 | 1084.661 | 1084.661
350 | 1081.662 | 1081.662
352 | 1076.872 | 1076.872
354 | 1070.898 | 1070.898
356 | 1065.018 | 1065.018
358 | 1059.58 | 1059.58
360 | 1055.284 | 1055.284
362 | 1050.886 | 1050.886
364 | 1052.647 | 1052.647
366 | 1051.117 | 1051.117
368 | 1048.266 | 1048.266
370 | 1040.172 | 1040.172
372 | 1033.483 | 1033.483
374 | 1030.95 | 1030.95
376 | 1032.263 | 1032.263
378 | 1031.391 | 1031.391
380 | 1025.791 | 1025.791
382 | 1020.911 | 1020.911
384 | 1015.65 | 1015.65
386 | 1012.139 | 1012.139
388 | 1010.472 | 1010.472
390 | 1005.401 | 1005.401
392 | 996.666 | 996.666
394 | 991.35 | 991.35
396 | 990.486 | 990.486
398 | 992.761 | 992.761
400 | 999.077 | 999.077
402 | 1001.8 | 1001.8
404 | 1002.224 | 1002.224
406 | 1002.003 | 1002.003
408 | 1003.596 | 1003.596
410 | 994.111 | 994.111
412 | 983.925 | 983.925
414 | 972.347 | 972.347
416 | 963.901 | 963.901
418 | 963.258 | 963.258
420 | 965.836 | 965.872
422 | 966.309 | 966.177
424 | 972.884 | 973.825
426 | 983.972 | 983.972
428 | 994.096 | 994.096
430 | 991.695 | 991.695
432 | 984.933 | 984.933
434 | 978.185 | 974.509
436 | 972.686 | 966.698
438 | 966.824 | 963.618
440 | 960.902 | 957.803
442 | 952.924 | 954.277
444 | 945.683 | 947.182
446 | 941.042 | 938.045
448 | 937.104 | 930.871
450 | 939.943 | 926.391
452 | 944.776 | 918.344
454 | 947.762 | 911.505
456 | 952.649 | 903.61
458 | 954.554 | 900.63
460 | 952.37 | 904.066
462 | 947.552 | 915.092
464 | 941.898 | 905.556
466 | 940.521 | 905.271
468 | 939.702 | 901.918
470 | 937.147 | 895.651
472 | 933.872 | 892.304
474 | 933.184 | 895.279
476 | 939.292 | 896.818
478 | 944.619 | 909.921
480 | 954.023 | 926.295
482 | 968.263 | 924.888
484 | 970.384 | 919.044
486 | 964.636 | 911.164
488 | 956.631 | 903.893
490 | 947.426 | 901.953
492 | 941.72 | 900.198
494 | 935.985 | 904.177
496 | 930.475 | 912.253
498 | 927.611 | 915.297
500 | 931.256 | 919.629
502 | 920.044
504 | 911.78
506 | 907.989
508 | 907.289
510 | 900.577
512 | 902.112
514 | 900.179
516 | 903.811
518 | 910.027
520 | 911.131 |  | End

## Flow Rate Calculations
Estimated Transfer Rate Demand | 100 | Mm3/a
Availible Days | 365
Pumping Hours | 24
Pf | 1.052
Pl | 1.02
PR | 1.2
Peak Design Flow | 4.0831 | m3/s

## Calculation Constants
Friction Factors
Ks (mm) - New | 0.03
Ks (mm) - Average | 0.06
Ks (mm) - Old | 0.15
Ks (mm) - Biofilm | 0.5
Kinemeatic Viscosity | 1.13e-06 | m2/s
Minor Loss - k | 150
Grade of Steel | X42
Yeild Capacity | 300 | Mpa
Design % of Yeild | 50%
Minimum D/t ratio | 160 | mm/mm

## Hydraulics
Option 2B |  |  |  | Option 2B | [12 empty] | Option 2B
Pump Station |  |  |  | Pipe Line | [9 empty] | Steel Pipeline Design |  |  | New Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Average Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Old Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Biofilm Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes
Name | Chainage (km) | Elevation (m) | Pumped Head (m) | Reference | Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Flow Rate (m3/s) | PipeVelocity (m/s) | Re | Static Head (m) | Dynamic Head (m) | Design Pressure (m) | Pipe Wall thickness (mm) | Steel Mass (kg) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m)
PS 1 | 8 | 1063.832 | 200 | Reservoir | 2 | 1069.018 | 0 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 10 | 10 | 10 | 13.75 | 0 | 0.008468 |  |  | 0 | 0 | 10 | 1079.018 | 0.0094904 |  |  | 0 | 0 | 10 | 1079.018 | 0.011153 |  |  | 0 | 0 | 10 | 1079.018 | 0.014105 |  |  | 0 | 0 | 10 | 1079.018
[5 empty] | 4 | 1067.321 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 11.697 | 11.209 | 11.697 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 11.209 | 1078.53 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 11.1544 | 1078.4754 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 11.0655 | 1078.3865 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 10.905 | 1078.226
[5 empty] | 6 | 1064.035 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 14.983 | 14.0071 | 14.983 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 14.0071 | 1078.0421 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 13.8977 | 1077.9327 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 13.72 | 1077.755 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 13.3989 | 1077.4339
|  |  |  | Pump Station | 8 | 1063.832 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 213.7221 | 213.5581 | 15.6609 | 1687279.6635 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 200 | 213.7221 | 1277.5541 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 200 | 213.5581 | 1277.3901 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 200 | 213.2915 | 1277.1235 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 200 | 212.8099 | 1276.6419
[5 empty] | 10 | 1067.893 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 209.1731 | 208.9545 | 15.3233 | 1651162.4615 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 209.1731 | 1277.0661 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 208.9545 | 1276.8475 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 208.599 | 1276.492 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 207.9568 | 1275.8498
Reservoirs |  |  |  |  | 12 | 1075.133 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 201.4451 | 201.1718 | 14.7526 | 1590079.2461 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 201.4451 | 1276.5781 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 201.1718 | 1276.3048 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 200.7275 | 1275.8605 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 199.9248 | 1275.0578
Name | Chainage (km) | Water Elevation (m) | Height |  | 14 | 1082.768 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 193.3222 | 192.9942 | 14.1529 | 1525861.1907 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 193.3222 | 1276.0902 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 192.9942 | 1275.7622 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 192.461 | 1275.229 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 191.4977 | 1274.2657
Supply Resrvoir | 2 | 1079.018 | 10 |  | 16 | 1089.726 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 185.8762 | 185.4936 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 185.8762 | 1275.6022 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 185.4936 | 1275.2196 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 184.8715 | 1274.5975 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 183.7477 | 1273.4737
BPT 2 | 330 | 1146.405 | 10 |  | 18 | 1094.131 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 180.9832 | 180.546 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 180.9832 | 1275.1142 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 180.546 | 1274.677 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 179.835 | 1273.966 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 178.5506 | 1272.6816
BPT 1 | 500 | 929.629 | 10 |  | 20 | 1097.897 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 176.7293 | 176.2373 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 176.7293 | 1274.6263 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 176.2373 | 1274.1343 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 175.4375 | 1273.3345 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 173.9926 | 1271.8896
[5 empty] | 22 | 1101.67 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 172.4683 | 171.9217 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 172.4683 | 1274.1383 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 171.9217 | 1273.5917 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 171.033 | 1272.703 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 169.4275 | 1271.0975
[5 empty] | 24 | 1095.952 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 177.6983 | 177.0971 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 177.6983 | 1273.6503 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 177.0971 | 1273.0491 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 176.1195 | 1272.0715 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 174.3535 | 1270.3055
[5 empty] | 26 | 1090.107 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 183.0553 | 182.3994 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 183.0553 | 1273.1623 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 182.3994 | 1272.5064 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 181.333 | 1271.44 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 179.4064 | 1269.5134
[5 empty] | 28 | 1085.781 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 186.8934 | 186.1828 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 186.8934 | 1272.6744 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 186.1828 | 1271.9638 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 185.0275 | 1270.8085 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 182.9404 | 1268.7214
|  | -67.387 |  |  | 30 | 1081.89 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 190.2964 | 189.5312 | 13.899 | 1498655.5949 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 190.2964 | 1272.1864 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 189.5312 | 1271.4212 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 188.287 | 1270.177 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 186.0393 | 1267.9293
[5 empty] | 32 | 1077.937 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 193.7614 | 192.9415 | 14.149 | 1525447.4405 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 193.7614 | 1271.6984 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 192.9415 | 1270.8785 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 191.6085 | 1269.5455 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 189.2003 | 1267.1373
[5 empty] | 34 | 1074.89 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 196.3205 | 195.4459 | 14.3327 | 1545117.826 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 196.3205 | 1271.2105 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 195.4459 | 1270.3359 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 194.024 | 1268.914 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 191.4552 | 1266.3452
[5 empty] | 36 | 1071.114 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 199.6085 | 198.6793 | 14.5698 | 1570509.1669 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 199.6085 | 1270.7225 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 198.6793 | 1269.7933 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 197.1685 | 1268.2825 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 194.4392 | 1265.5532
Route | Botswana 2 |  |  |  | 38 | 1065.311 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 204.9235 | 203.9397 | 14.9556 | 1611806.4923 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 204.9235 | 1270.2345 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 203.9397 | 1269.2507 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 202.34 | 1267.651 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 199.4501 | 1264.7611
Option | 2B |  |  |  | 40 | 1059.051 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 210.6956 | 209.657 | 15.3748 | 1656674.9172 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 210.6956 | 1269.7466 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 209.657 | 1268.708 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 207.9685 | 1267.0195 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 204.9181 | 1263.9691
[5 empty] | 42 | 1054.28 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 214.9786 | 213.8854 | 15.6849 | 1689846.904 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 214.9786 | 1269.2586 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 213.8854 | 1268.1654 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 212.108 | 1266.388 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 208.897 | 1263.177
[5 empty] | 44 | 1053.871 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 214.8996 | 213.7518 | 15.6751 | 1688798.7057 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 214.8996 | 1268.7706 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 213.7518 | 1267.6228 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 211.8855 | 1265.7565 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 208.514 | 1262.385
[5 empty] | 46 | 1050.42 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 217.8626 | 216.6601 | 15.8884 | 1711609.8598 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 217.8626 | 1268.2826 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 216.6601 | 1267.0801 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 214.705 | 1265.125 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 211.1729 | 1261.5929
[5 empty] | 48 | 1052.704 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 215.0907 | 213.8335 | 15.6811 | 1689439.8714 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 215.0907 | 1267.7947 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 213.8335 | 1266.5375 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 211.7895 | 1264.4935 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 208.0969 | 1260.8009
[5 empty] | 50 | 1056.355 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 210.9517 | 209.6399 | 15.3736 | 1656540.3415 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 210.9517 | 1267.3067 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 209.6399 | 1265.9949 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 207.507 | 1263.862 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 203.6538 | 1260.0088
[5 empty] | 52 | 1058.466 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 208.3527 | 206.9862 | 15.179 | 1635717.4756 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 208.3527 | 1266.8187 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 206.9862 | 1265.4522 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 204.7645 | 1263.2305 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 200.7508 | 1259.2168
[5 empty] | 54 | 1055.99 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 210.3408 | 208.9196 | 15.3208 | 1650888.872 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 210.3408 | 1266.3308 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 208.9196 | 1264.9096 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 206.609 | 1262.599 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 202.4347 | 1258.4247
[5 empty] | 56 | 1055.66 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 210.1828 | 208.707 | 15.3052 | 1649220.4319 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 210.1828 | 1265.8428 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 208.707 | 1264.367 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 206.3075 | 1261.9675 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 201.9727 | 1257.6327
[5 empty] | 58 | 1056.404 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 208.9508 | 207.4204 | 15.2108 | 1639124.1565 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 208.9508 | 1265.3548 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 207.4204 | 1263.8244 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 204.932 | 1261.336 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 200.4366 | 1256.8406
[5 empty] | 60 | 1056.841 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 208.0258 | 206.4407 | 15.139 | 1631436.3421 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 208.0258 | 1264.8668 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 206.4407 | 1263.2817 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 203.8635 | 1260.7045 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 199.2076 | 1256.0486
[5 empty] | 62 | 1056.377 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 208.0019 | 206.3621 | 15.1332 | 1630819.2552 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 208.0019 | 1264.3789 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 206.3621 | 1262.7391 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 203.696 | 1260.073 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 198.8795 | 1255.2565
[5 empty] | 64 | 1052.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 211.3879 | 209.6935 | 15.3775 | 1656960.8021 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 211.3879 | 1263.8909 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 209.6935 | 1262.1965 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 206.9385 | 1259.4415 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 201.9615 | 1254.4645
[5 empty] | 66 | 1046.022 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 217.3809 | 215.6318 | 15.813 | 1703545.1032 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 217.3809 | 1263.4029 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 215.6318 | 1261.6538 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 212.788 | 1258.81 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 207.6504 | 1253.6724
[5 empty] | 68 | 1036.575 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 226.34 | 224.5362 | 16.466 | 1773361.5142 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 226.34 | 1262.915 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 224.5362 | 1261.1112 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 221.6035 | 1258.1785 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 216.3054 | 1252.8804
[5 empty] | 70 | 1031.818 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 230.609 | 228.7506 | 16.775 | 1806390.4197 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 230.609 | 1262.427 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 228.7506 | 1260.5686 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 225.729 | 1257.547 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 220.2703 | 1252.0883
[5 empty] | 72 | 1027.675 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 234.264 | 232.3509 | 17.0391 | 1834599.8145 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 234.264 | 1261.939 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 232.3509 | 1260.0259 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 229.2405 | 1256.9155 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 223.6213 | 1251.2963
[5 empty] | 74 | 1023.844 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 237.607 | 235.6393 | 17.2802 | 1860358.6374 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 237.607 | 1261.451 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 235.6393 | 1259.4833 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 232.44 | 1256.284 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 226.6602 | 1250.5042
[5 empty] | 76 | 1020.888 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 240.0751 | 238.0527 | 17.4572 | 1879259.6632 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 240.0751 | 1260.9631 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 238.0527 | 1258.9407 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 234.7645 | 1255.6525 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 228.8242 | 1249.7122
[5 empty] | 78 | 1023.648 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 236.8271 | 234.75 | 17.215 | 1853393.3478 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 236.8271 | 1260.4751 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 234.75 | 1258.398 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 231.373 | 1255.021 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 225.2721 | 1248.9201
[5 empty] | 80 | 1027.566 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 232.4211 | 230.2894 | 16.8879 | 1818448.351 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 232.4211 | 1259.9871 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 230.2894 | 1257.8554 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 226.8235 | 1254.3895 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 220.5621 | 1248.1281
[5 empty] | 82 | 1032.371 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 227.1282 | 224.9418 | 16.4957 | 1776540.6004 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 227.1282 | 1259.4992 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 224.9418 | 1257.3128 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 221.387 | 1253.758 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 214.965 | 1247.336
[5 empty] | 84 | 1034.983 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 224.0282 | 221.7872 | 16.2644 | 1751811.6087 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 224.0282 | 1259.0112 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 221.7872 | 1256.7702 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 218.1435 | 1253.1265 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 211.561 | 1246.544
[5 empty] | 86 | 1033.213 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 225.3102 | 223.0145 | 16.3544 | 1761433.5265 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 225.3102 | 1258.5232 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 223.0145 | 1256.2275 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 219.282 | 1252.495 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 212.5389 | 1245.7519
[5 empty] | 88 | 1031.188 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 226.8473 | 224.4969 | 16.4631 | 1773053.4416 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 226.8473 | 1258.0353 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 224.4969 | 1255.6849 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 220.6755 | 1251.8635 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 213.7719 | 1244.9599
[5 empty] | 90 | 1029.08 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 228.4673 | 226.0623 | 16.5779 | 1785322.707 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 228.4673 | 1257.5473 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 226.0623 | 1255.1423 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 222.152 | 1251.232 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 215.0878 | 1244.1678
[5 empty] | 92 | 1026.322 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 230.7373 | 228.2776 | 16.7404 | 1802684.4083 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 230.7373 | 1257.0593 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 228.2776 | 1254.5996 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 224.2785 | 1250.6005 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 217.0538 | 1243.3758
[5 empty] | 94 | 1023.207 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 233.3643 | 230.85 | 16.929 | 1822840.6275 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 233.3643 | 1256.5713 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 230.85 | 1254.057 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 226.762 | 1249.969 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 219.3767 | 1242.5837
[5 empty] | 96 | 1021.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 234.5804 | 232.0114 | 17.0142 | 1831939.5775 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 234.5804 | 1256.0834 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 232.0114 | 1253.5144 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 227.8345 | 1249.3375 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 220.2887 | 1241.7917
[5 empty] | 98 | 1019.765 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 235.8304 | 233.2067 | 17.1018 | 1841304.1591 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 235.8304 | 1255.5954 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 233.2067 | 1252.9717 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 228.941 | 1248.706 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 221.2346 | 1240.9996
[5 empty] | 100 | 1018.493 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 236.6144 | 233.9361 | 17.1553 | 1847017.7026 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 236.6144 | 1255.1074 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 233.9361 | 1252.4291 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 229.5815 | 1248.0745 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 221.7146 | 1240.2076
[5 empty] | 102 | 1016.444 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 238.1755 | 235.4425 | 17.2658 | 1858817.0103 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 238.1755 | 1254.6195 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 235.4425 | 1251.8865 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 230.999 | 1247.443 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 222.9715 | 1239.4155
[5 empty] | 104 | 1013.288 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 240.8435 | 238.0559 | 17.4574 | 1879284.5301 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 240.8435 | 1254.1315 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 238.0559 | 1251.3439 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 233.5235 | 1246.8115 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 225.3355 | 1238.6235
[5 empty] | 106 | 1007.843 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 245.8005 | 242.9582 | 17.8169 | 1917669.3819 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 245.8005 | 1253.6435 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 242.9582 | 1250.8012 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 238.337 | 1246.18 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 229.9884 | 1237.8314
[5 empty] | 108 | 1001.282 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 251.8735 | 248.9766 | 18.2583 | 1964774.9202 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 251.8735 | 1253.1555 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 248.9766 | 1250.2586 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 244.2665 | 1245.5485 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 235.7574 | 1237.0394
[5 empty] | 110 | 996.609 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 256.0586 | 253.107 | 18.5612 | 1997092.0395 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 256.0586 | 1252.6676 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 253.107 | 1249.716 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 248.308 | 1244.917 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 239.6383 | 1236.2473
[5 empty] | 112 | 992.999 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 259.1806 | 256.1743 | 18.7861 | 2021086.1057 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 259.1806 | 1252.1796 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 256.1743 | 1249.1733 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 251.2865 | 1244.2855 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 242.4563 | 1235.4553
[5 empty] | 114 | 993.639 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 258.0526 | 254.9917 | 18.6994 | 2011835.7381 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 258.0526 | 1251.6916 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 254.9917 | 1248.6307 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 250.015 | 1243.654 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 241.0242 | 1234.6632
[5 empty] | 116 | 994.611 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 256.5927 | 253.4771 | 18.5883 | 1999987.4298 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 256.5927 | 1251.2037 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 253.4771 | 1248.0881 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 248.4115 | 1243.0225 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 239.2602 | 1233.8712
[5 empty] | 118 | 995.751 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 254.9647 | 251.7944 | 18.4649 | 1986823.5019 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 254.9647 | 1250.7157 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 251.7944 | 1247.5454 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 246.64 | 1242.391 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 237.3281 | 1233.0791
[5 empty] | 120 | 996.479 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 253.7487 | 250.5238 | 18.3717 | 1976881.8288 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 253.7487 | 1250.2277 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 250.5238 | 1247.0028 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 245.2805 | 1241.7595 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 235.8081 | 1232.2871
[5 empty] | 122 | 996.147 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 253.5927 | 250.3132 | 18.3563 | 1975233.731 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 253.5927 | 1249.7397 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 250.3132 | 1246.4602 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 244.981 | 1241.128 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 235.348 | 1231.495
[5 empty] | 124 | 992.094 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 257.1578 | 253.8235 | 18.6137 | 2002697.8924 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 257.1578 | 1249.2518 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 253.8235 | 1245.9175 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 248.4025 | 1240.4965 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 238.609 | 1230.703
[5 empty] | 126 | 985.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 263.1408 | 259.7519 | 19.0485 | 2049064.9746 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 263.1408 | 1248.7638 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 259.7519 | 1245.3749 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 254.242 | 1239.865 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 244.2879 | 1229.9109
[5 empty] | 128 | 977.759 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 270.5168 | 267.0733 | 19.5854 | 2106301.2854 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 270.5168 | 1248.2758 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 267.0733 | 1244.8323 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 261.4745 | 1239.2335 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 251.3599 | 1229.1189
[5 empty] | 130 | 969.772 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 278.0159 | 274.5177 | 20.1313 | 2164470.0174 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 278.0159 | 1247.7879 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 274.5177 | 1244.2897 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 268.83 | 1238.602 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 258.5548 | 1228.3268
[5 empty] | 132 | 981.785 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 265.5149 | 261.962 | 19.2105 | 2066345.952 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 265.5149 | 1247.2999 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 261.962 | 1243.747 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 256.1855 | 1237.9705 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 245.7498 | 1227.5348
[5 empty] | 134 | 991.458 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 255.3539 | 251.7464 | 18.4614 | 1986447.622 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 255.3539 | 1246.8119 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 251.7464 | 1243.2044 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 245.881 | 1237.339 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 235.2847 | 1226.7427
[5 empty] | 136 | 987.77 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 258.5539 | 254.8918 | 18.6921 | 2011054.0374 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 258.5539 | 1246.3239 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 254.8918 | 1242.6618 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 248.9375 | 1236.7075 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 238.1807 | 1225.9507
[5 empty] | 138 | 982.725 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 263.111 | 259.3941 | 19.0222 | 2046267.2118 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 263.111 | 1245.836 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 259.3941 | 1242.1191 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 253.351 | 1236.076 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 242.4336 | 1225.1586
[5 empty] | 140 | 977.559 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 267.789 | 264.0175 | 19.3613 | 2082415.5397 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 267.789 | 1245.348 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 264.0175 | 1241.5765 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 257.8855 | 1235.4445 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 246.8076 | 1224.3666
[5 empty] | 142 | 975.289 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 269.571 | 265.7449 | 19.488 | 2095918.261 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 269.571 | 1244.86 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 265.7449 | 1241.0339 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 259.524 | 1234.813 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 248.2855 | 1223.5745
[5 empty] | 144 | 973.968 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 270.4041 | 266.5232 | 19.545 | 2102002.202 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 270.4041 | 1244.3721 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 266.5232 | 1240.4912 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 260.2135 | 1234.1815 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 248.8145 | 1222.7825
[5 empty] | 146 | 962.473 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 281.4111 | 277.4756 | 20.3482 | 2187574.7097 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 281.4111 | 1243.8841 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 277.4756 | 1239.9486 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 271.077 | 1233.55 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 259.5174 | 1221.9904
[5 empty] | 148 | 951.285 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 292.1111 | 288.121 | 21.1289 | 2270687.5956 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 292.1111 | 1243.3961 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 288.121 | 1239.406 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 281.6335 | 1232.9185 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 269.9134 | 1221.1984
[5 empty] | 150 | 948.174 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 294.7342 | 290.6894 | 21.3172 | 2290730.9377 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 294.7342 | 1242.9082 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 290.6894 | 1238.8634 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 284.113 | 1232.287 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 272.2323 | 1220.4063
[5 empty] | 152 | 944.641 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 297.7792 | 293.6797 | 21.5365 | 2314063.1234 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 297.7792 | 1242.4202 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 293.6797 | 1238.3207 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 287.0145 | 1231.6555 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 274.9733 | 1219.6143
[5 empty] | 154 | 941.566 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 300.3662 | 296.2121 | 21.7222 | 2333818.081 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 300.3662 | 1241.9322 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 296.2121 | 1237.7781 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 289.458 | 1231.024 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 277.2562 | 1218.8222
[5 empty] | 156 | 940.942 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 300.5022 | 296.2935 | 21.7282 | 2334452.7875 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 300.5022 | 1241.4442 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 296.2935 | 1237.2355 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 289.4505 | 1230.3925 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 277.0882 | 1218.0302
[5 empty] | 158 | 939.726 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 301.2303 | 296.9668 | 21.7776 | 2339705.1272 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 301.2303 | 1240.9563 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 296.9668 | 1236.6928 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 290.035 | 1229.761 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 277.5121 | 1217.2381
[5 empty] | 160 | 936.738 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 303.7303 | 299.4122 | 21.9569 | 2358777.1921 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 303.7303 | 1240.4683 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 299.4122 | 1236.1502 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 292.3915 | 1229.1295 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 279.7081 | 1216.4461
[5 empty] | 162 | 933.65 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 306.3303 | 301.9576 | 22.1436 | 2378625.813 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 306.3303 | 1239.9803 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 301.9576 | 1235.6076 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 294.848 | 1228.498 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 282.004 | 1215.654
[5 empty] | 164 | 932.745 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 306.7474 | 302.3199 | 22.1701 | 2381451.2677 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 306.7474 | 1239.4924 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 302.3199 | 1235.0649 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 295.1215 | 1227.8665 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 282.117 | 1214.862
[5 empty] | 166 | 931.696 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.3084 | 302.8263 | 22.2073 | 2385399.397 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 307.3084 | 1239.0044 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 302.8263 | 1234.5223 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 295.539 | 1227.235 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 282.3739 | 1214.0699
[5 empty] | 168 | 930.999 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.5174 | 302.9807 | 22.2186 | 2386602.9796 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 307.5174 | 1238.5164 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 302.9807 | 1233.9797 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 295.6045 | 1226.6035 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 282.2789 | 1213.2779
[5 empty] | 170 | 930.885 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.1434 | 302.5521 | 22.1872 | 2383261.0225 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 307.1434 | 1238.0284 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 302.5521 | 1233.4371 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 295.087 | 1225.972 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 281.6009 | 1212.4859
[5 empty] | 172 | 930.378 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.1625 | 302.5164 | 22.1845 | 2382983.2146 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 307.1625 | 1237.5405 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 302.5164 | 1232.8944 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 294.9625 | 1225.3405 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 281.3158 | 1211.6938
[5 empty] | 174 | 931.324 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 305.7285 | 301.0278 | 22.0754 | 2371375.8343 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 305.7285 | 1237.0525 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 301.0278 | 1232.3518 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 293.385 | 1224.709 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 279.5778 | 1210.9018
[5 empty] | 176 | 933.53 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 303.0345 | 298.2792 | 21.8738 | 2349940.6965 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 303.0345 | 1236.5645 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 298.2792 | 1231.8092 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 290.5475 | 1224.0775 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 276.5797 | 1210.1097
[5 empty] | 178 | 932.714 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 303.3626 | 298.5525 | 21.8939 | 2352072.7438 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 303.3626 | 1236.0766 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 298.5525 | 1231.2665 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 290.732 | 1223.446 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 276.6037 | 1209.3177
[5 empty] | 180 | 928.311 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.2776 | 302.4129 | 22.1769 | 2382176.06 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 307.2776 | 1235.5886 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 302.4129 | 1230.7239 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 294.5035 | 1222.8145 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 280.2146 | 1208.5256
[5 empty] | 182 | 924.179 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 310.9216 | 306.0023 | 22.4402 | 2410159.0148 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 310.9216 | 1235.1006 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 306.0023 | 1230.1813 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 298.004 | 1222.183 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 283.5546 | 1207.7336
[5 empty] | 184 | 928.398 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 306.2146 | 301.2406 | 22.091 | 2373035.5606 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 306.2146 | 1234.6126 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 301.2406 | 1229.6386 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 293.1535 | 1221.5515 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 278.5435 | 1206.9415
[5 empty] | 186 | 930.866 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 303.2587 | 298.23 | 21.8702 | 2349557.3519 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 303.2587 | 1234.1247 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 298.23 | 1229.096 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 290.054 | 1220.92 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 275.2835 | 1206.1495
[5 empty] | 188 | 928.411 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 305.2257 | 300.1424 | 22.0104 | 2364471.402 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 305.2257 | 1233.6367 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 300.1424 | 1228.5534 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 291.8775 | 1220.2885 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 276.9464 | 1205.3574
[5 empty] | 190 | 927.849 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 305.2997 | 300.1617 | 22.0119 | 2364622.4508 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 305.2997 | 1233.1487 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 300.1617 | 1228.0107 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 291.808 | 1219.657 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 276.7164 | 1204.5654
[5 empty] | 192 | 926.71 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 305.9508 | 300.7581 | 22.0556 | 2369272.9724 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 305.9508 | 1232.6608 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 300.7581 | 1227.4681 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 292.3155 | 1219.0255 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 277.0633 | 1203.7733
[5 empty] | 194 | 926.201 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 305.9718 | 300.7245 | 22.0531 | 2369010.7264 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 305.9718 | 1232.1728 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 300.7245 | 1226.9255 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 292.193 | 1218.394 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 276.7803 | 1202.9813
[5 empty] | 196 | 924.509 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.1758 | 301.8739 | 22.1374 | 2377973.059 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 307.1758 | 1231.6848 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 301.8739 | 1226.3829 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 293.2535 | 1217.7625 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 277.6802 | 1202.1892
[5 empty] | 198 | 923.417 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.7799 | 302.4232 | 22.1777 | 2382256.58 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 307.7799 | 1231.1969 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 302.4232 | 1225.8402 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 293.714 | 1217.131 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 277.9802 | 1201.3972
[5 empty] | 200 | 923.011 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.6979 | 302.2866 | 22.1677 | 2381191.267 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 307.6979 | 1230.7089 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 302.2866 | 1225.2976 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 293.4885 | 1216.4995 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 277.5941 | 1200.6051
[5 empty] | 202 | 921.969 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 308.2519 | 302.786 | 22.2043 | 2385084.8275 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 308.2519 | 1230.2209 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 302.786 | 1224.755 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 293.899 | 1215.868 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 277.8441 | 1199.8131
[5 empty] | 204 | 920.661 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 309.0719 | 303.5513 | 22.2604 | 2391052.1201 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 309.0719 | 1229.7329 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 303.5513 | 1224.2123 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 294.5755 | 1215.2365 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 278.36 | 1199.021
[5 empty] | 206 | 920.243 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 309.002 | 303.4267 | 22.2513 | 2390080.4466 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 309.002 | 1229.245 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 303.4267 | 1223.6697 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 294.362 | 1214.605 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 277.986 | 1198.229
[5 empty] | 208 | 919.297 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 309.46 | 303.8301 | 22.2809 | 2393225.2662 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 309.46 | 1228.757 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 303.8301 | 1223.1271 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 294.6765 | 1213.9735 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 278.1399 | 1197.4369
[5 empty] | 210 | 917.533 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 310.736 | 305.0514 | 22.3704 | 2402746.9909 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 310.736 | 1228.269 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 305.0514 | 1222.5844 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 295.809 | 1213.342 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 279.1119 | 1196.6449
[5 empty] | 212 | 917.684 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 310.0971 | 304.3578 | 22.3196 | 2397339.5875 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 310.0971 | 1227.7811 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 304.3578 | 1222.0418 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 295.0265 | 1212.7105 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 278.1688 | 1195.8528
[5 empty] | 214 | 915.724 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 311.5691 | 305.7752 | 22.4235 | 2408388.846 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 311.5691 | 1227.2931 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 305.7752 | 1221.4992 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 296.355 | 1212.079 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 279.3368 | 1195.0608
[5 empty] | 216 | 915.73 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 311.0751 | 305.2266 | 22.3833 | 2404112.0654 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 311.0751 | 1226.8051 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 305.2266 | 1220.9566 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 295.7175 | 1211.4475 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 278.5387 | 1194.2687
[5 empty] | 218 | 915.584 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 310.7331 | 304.8299 | 22.3542 | 2401020.0827 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 310.7331 | 1226.3171 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 304.8299 | 1220.4139 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 295.232 | 1210.816 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 277.8927 | 1193.4767
[5 empty] | 220 | 915.444 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 310.3852 | 304.4273 | 22.3247 | 2397881.2409 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 310.3852 | 1225.8292 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 304.4273 | 1219.8713 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 294.7405 | 1210.1845 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 277.2406 | 1192.6846
[5 empty] | 222 | 913.52 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 311.8212 | 305.8087 | 22.426 | 2408649.8198 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 311.8212 | 1225.3412 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 305.8087 | 1219.3287 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 296.033 | 1209.553 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 278.3726 | 1191.8926
[5 empty] | 224 | 912.524 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 312.3292 | 306.262 | 22.4592 | 2412183.879 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 312.3292 | 1224.8532 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 306.262 | 1218.786 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 296.3975 | 1208.9215 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 278.5765 | 1191.1005
[5 empty] | 226 | 912.565 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 311.8003 | 305.6784 | 22.4164 | 2407634.4055 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 311.8003 | 1224.3653 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 305.6784 | 1218.2434 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 295.725 | 1208.29 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 277.7435 | 1190.3085
[5 empty] | 228 | 913.484 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 310.3933 | 304.2168 | 22.3092 | 2396240.0161 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 310.3933 | 1223.8773 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 304.2168 | 1217.7008 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 294.1745 | 1207.6585 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 276.0324 | 1189.5164
[5 empty] | 230 | 913.545 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 309.8443 | 303.6131 | 22.265 | 2391533.9818 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 309.8443 | 1223.3893 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 303.6131 | 1217.1581 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 293.482 | 1207.027 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 275.1794 | 1188.7244
[5 empty] | 232 | 914.546 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 308.3553 | 302.0695 | 22.1518 | 2379498.6226 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 308.3553 | 1222.9013 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 302.0695 | 1216.6155 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 291.8495 | 1206.3955 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 273.3863 | 1187.9323
[5 empty] | 234 | 918.285 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 304.1284 | 297.7879 | 21.8378 | 2346109.0406 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 304.1284 | 1222.4134 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 297.7879 | 1216.0729 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 287.479 | 1205.764 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 268.8553 | 1187.1403
[5 empty] | 236 | 919.357 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 302.5684 | 296.1733 | 21.7194 | 2333515.0892 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 302.5684 | 1221.9254 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 296.1733 | 1215.5303 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 285.7755 | 1205.1325 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 266.9912 | 1186.3482
[5 empty] | 238 | 918.649 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 302.7884 | 296.3386 | 21.7315 | 2334805.0193 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 302.7884 | 1221.4374 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 296.3386 | 1214.9876 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 285.852 | 1204.501 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 266.9072 | 1185.5562
[5 empty] | 240 | 922.974 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 297.9755 | 291.471 | 21.3745 | 2296830.0585 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 297.9755 | 1220.9495 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 291.471 | 1214.445 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 280.8955 | 1203.8695 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 261.7901 | 1184.7641
[5 empty] | 242 | 927.375 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 293.0865 | 286.5274 | 21.012 | 2258249.316 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 293.0865 | 1220.4615 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 286.5274 | 1213.9024 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 275.863 | 1203.238 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 256.5971 | 1183.9721
[5 empty] | 244 | 929.253 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 290.7205 | 284.1067 | 20.8345 | 2239353.6697 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 290.7205 | 1219.9735 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 284.1067 | 1213.3597 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 273.3535 | 1202.6065 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 253.927 | 1183.18
[5 empty] | 246 | 930.863 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 288.6226 | 281.9541 | 20.6766 | 2222547.4429 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 288.6226 | 1219.4856 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 281.9541 | 1212.8171 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 271.112 | 1201.975 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 251.525 | 1182.388
[5 empty] | 248 | 931.924 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 287.0736 | 280.3505 | 20.559 | 2210025.825 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 287.0736 | 1218.9976 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 280.3505 | 1212.2745 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 269.4195 | 1201.3435 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 249.6719 | 1181.5959
[5 empty] | 250 | 936.722 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 281.7876 | 275.0098 | 20.1674 | 2168314.7733 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 281.7876 | 1218.5096 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 275.0098 | 1211.7318 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 263.99 | 1200.712 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 244.0819 | 1180.8039
[5 empty] | 252 | 941.777 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 276.2446 | 269.4122 | 19.7569 | 2124580.276 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 276.2446 | 1218.0216 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 269.4122 | 1211.1892 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 258.3035 | 1200.0805 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 238.2348 | 1180.0118
[5 empty] | 254 | 948.143 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 269.3907 | 262.5036 | 19.2503 | 2070579.9683 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 269.3907 | 1217.5337 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 262.5036 | 1210.6466 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 251.306 | 1199.449 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 231.0768 | 1179.2198
[5 empty] | 256 | 955.417 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 261.6287 | 254.6869 | 18.677 | 2009451.8796 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 261.6287 | 1217.0457 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 254.6869 | 1210.1039 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 243.4005 | 1198.8175 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 223.0107 | 1178.4277
[5 empty] | 258 | 962.7 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 253.8577 | 246.8613 | 18.1032 | 1948220.9394 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 253.8577 | 1216.5577 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 246.8613 | 1209.5613 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 235.486 | 1198.186 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 214.9357 | 1177.6357
[5 empty] | 260 | 969.281 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 246.7888 | 239.7377 | 17.5808 | 1892454.4879 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 246.7888 | 1216.0698 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 239.7377 | 1209.0187 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 228.2735 | 1197.5545 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 207.5626 | 1176.8436
[5 empty] | 262 | 980.284 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 235.2978 | 228.1921 | 16.7341 | 1802013.7873 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 235.2978 | 1215.5818 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 228.1921 | 1208.4761 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 216.639 | 1196.923 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 195.7676 | 1176.0516
[5 empty] | 264 | 986.551 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 228.5428 | 221.3824 | 16.2347 | 1748638.5704 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 228.5428 | 1215.0938 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 221.3824 | 1207.9334 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 209.7405 | 1196.2915 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 188.7085 | 1175.2595
[5 empty] | 266 | 989.198 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 225.4078 | 218.1928 | 16.0008 | 1723629.1631 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 225.4078 | 1214.6058 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 218.1928 | 1207.3908 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 206.462 | 1195.66 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 185.2695 | 1174.4675
[5 empty] | 268 | 994.39 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 219.7279 | 212.4582 | 15.5803 | 1678651.2223 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 219.7279 | 1214.1179 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 212.4582 | 1206.8482 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 200.6385 | 1195.0285 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 179.2854 | 1173.6754
[5 empty] | 270 | 999.917 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 213.7129 | 206.3885 | 15.1352 | 1631026.8 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 213.7129 | 1213.6299 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 206.3885 | 1206.3055 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 194.48 | 1194.397 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 172.9664 | 1172.8834
[5 empty] | 272 | 1004.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 208.5189 | 201.1399 | 14.7503 | 1589828.4709 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 208.5189 | 1213.1419 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 201.1399 | 1205.7629 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 189.1425 | 1193.7655 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 167.4683 | 1172.0913
[5 empty] | 274 | 1008.819 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 203.835 | 196.4013 | 14.4028 | 1552620.7565 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 203.835 | 1212.654 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 196.4013 | 1205.2203 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 184.315 | 1193.134 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 162.4803 | 1171.2993
[5 empty] | 276 | 1007.834 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 204.332 | 196.8436 | 14.4352 | 1556094.7463 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 204.332 | 1212.166 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 196.8436 | 1204.6776 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 184.6685 | 1192.5025 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 162.6732 | 1170.5072
[5 empty] | 278 | 1005.626 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 206.052 | 198.509 | 14.5573 | 1569172.1918 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 206.052 | 1211.678 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 198.509 | 1204.135 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 186.245 | 1191.871 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 164.0892 | 1169.7152
[5 empty] | 280 | 1001.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 209.567 | 201.9694 | 14.8111 | 1596340.3105 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 209.567 | 1211.19 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 201.9694 | 1203.5924 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 189.6165 | 1191.2395 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 167.3001 | 1168.9231
[5 empty] | 282 | 1004.052 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 206.6501 | 198.9978 | 14.5932 | 1573009.7764 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 206.6501 | 1210.7021 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 198.9978 | 1203.0498 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 186.556 | 1190.608 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 164.0791 | 1168.1311
[5 empty] | 284 | 1010.797 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 199.4171 | 191.7101 | 14.0587 | 1515774.111 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 199.4171 | 1210.2141 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 191.7101 | 1202.5071 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 179.1795 | 1189.9765 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 156.542 | 1167.339
[5 empty] | 286 | 1014.67 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 195.0561 | 187.2945 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 195.0561 | 1209.7261 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 187.2945 | 1201.9645 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 174.675 | 1189.345 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 151.877 | 1166.547
[5 empty] | 288 | 1017.319 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 191.9192 | 184.1029 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 191.9192 | 1209.2382 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 184.1029 | 1201.4219 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 171.3945 | 1188.7135 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 148.4359 | 1165.7549
[5 empty] | 290 | 1027.459 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 181.2912 | 173.4202 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 181.2912 | 1208.7502 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 173.4202 | 1200.8792 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 160.623 | 1188.082 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 137.5039 | 1164.9629
[5 empty] | 292 | 1031.99 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 176.2722 | 168.3466 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 176.2722 | 1208.2622 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 168.3466 | 1200.3366 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 155.4605 | 1187.4505 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 132.1808 | 1164.1708
[5 empty] | 294 | 1036.254 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 171.5202 | 163.54 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 171.5202 | 1207.7742 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 163.54 | 1199.794 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 150.565 | 1186.819 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 127.1248 | 1163.3788
[5 empty] | 296 | 1040.127 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 167.1593 | 159.1243 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 167.1593 | 1207.2863 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 159.1243 | 1199.2513 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 146.0605 | 1186.1875 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 122.4597 | 1162.5867
[5 empty] | 298 | 1044.396 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 162.4023 | 154.3127 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 162.4023 | 1206.7983 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 154.3127 | 1198.7087 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 141.16 | 1185.556 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 117.3987 | 1161.7947
[5 empty] | 300 | 1051.339 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 154.9713 | 146.8271 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 154.9713 | 1206.3103 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 146.8271 | 1198.1661 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 133.5855 | 1184.9245 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 109.6636 | 1161.0026
[5 empty] | 302 | 1060.955 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 144.8674 | 136.6685 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 144.8674 | 1205.8224 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 136.6685 | 1197.6235 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 123.338 | 1184.293 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 99.2556 | 1160.2106
[5 empty] | 304 | 1070.227 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 135.1074 | 126.8538 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 135.1074 | 1205.3344 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 126.8538 | 1197.0808 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 113.4345 | 1183.6615 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 89.1915 | 1159.4185
[5 empty] | 306 | 1072.691 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 132.1554 | 123.8472 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 132.1554 | 1204.8464 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 123.8472 | 1196.5382 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 110.339 | 1183.03 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 85.9355 | 1158.6265
[5 empty] | 308 | 1076.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 127.8555 | 119.4926 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 127.8555 | 1204.3585 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 119.4926 | 1195.9956 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 105.8955 | 1182.3985 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 81.3314 | 1157.8344
[5 empty] | 310 | 1083.996 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 119.8745 | 111.4569 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 119.8745 | 1203.8705 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 111.4569 | 1195.4529 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 97.771 | 1181.767 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 73.0464 | 1157.0424
[5 empty] | 312 | 1097.188 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 106.1945 | 97.7223 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 106.1945 | 1203.3825 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 97.7223 | 1194.9103 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 83.9475 | 1181.1355 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 59.0623 | 1156.2503
[5 empty] | 314 | 1103.545 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 99.3495 | 90.8227 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 99.3495 | 1202.8945 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 90.8227 | 1194.3677 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 76.959 | 1180.504 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 51.9133 | 1155.4583
[5 empty] | 316 | 1105.174 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 97.2326 | 88.651 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 97.2326 | 1202.4066 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 88.651 | 1193.825 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 74.6985 | 1179.8725 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 49.4922 | 1154.6662
[5 empty] | 318 | 1111.657 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 90.2616 | 81.6254 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 90.2616 | 1201.9186 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 81.6254 | 1193.2824 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 67.584 | 1179.241 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 42.2172 | 1153.8742
[5 empty] | 320 | 1122.935 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 78.4956 | 69.8048 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 78.4956 | 1201.4306 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 69.8048 | 1192.7398 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 55.6745 | 1178.6095 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 30.1471 | 1153.0821
[5 empty] | 322 | 1128.197 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 72.7457 | 64.0001 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 72.7457 | 1200.9427 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 64.0001 | 1192.1971 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 49.781 | 1177.978 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 24.0931 | 1152.2901
[5 empty] | 324 | 1132.561 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 67.8937 | 59.0935 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 67.8937 | 1200.4547 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 59.0935 | 1191.6545 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 44.7855 | 1177.3465 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 18.937 | 1151.498
[5 empty] | 326 | 1131.854 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 68.1127 | 59.2579 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 68.1127 | 1199.9667 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 59.2579 | 1191.1119 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 44.861 | 1176.715 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 18.852 | 1150.706
[5 empty] | 328 | 1133.338 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 66.1407 | 57.2313 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 66.1407 | 1199.4787 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 57.2313 | 1190.5693 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 42.7455 | 1176.0835 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 16.5759 | 1149.9139
|  |  |  | Reservoir | 330 | 1136.405 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 10 | 10 | 10 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 10 | 1146.405 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 10 | 1146.405 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 10 | 1146.405 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 10 | 1146.405
[5 empty] | 332 | 1128.709 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 17.696 | 16.342 | 17.696 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 16.342 | 1145.051 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 16.1853 | 1144.8943 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 15.9296 | 1144.6386 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 15.463 | 1144.172
[5 empty] | 334 | 1120.713 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 25.692 | 22.984 | 25.692 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 22.984 | 1143.697 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 22.6706 | 1143.3836 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 22.1591 | 1142.8721 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 21.2259 | 1141.9389
[5 empty] | 336 | 1115.226 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 31.179 | 27.1171 | 31.179 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 27.1171 | 1142.3431 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 26.6469 | 1141.8729 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 25.8797 | 1141.1057 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 24.4799 | 1139.7059
[5 empty] | 338 | 1108.709 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 37.696 | 32.2801 | 37.696 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 32.2801 | 1140.9891 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 31.6532 | 1140.3622 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 30.6303 | 1139.3393 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 28.7638 | 1137.4728
[5 empty] | 340 | 1102.499 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 43.906 | 37.1361 | 43.906 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 37.1361 | 1139.6351 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 36.3525 | 1138.8515 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 35.0739 | 1137.5729 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 32.7408 | 1135.2398
[5 empty] | 342 | 1096.349 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 50.056 | 41.9321 | 50.056 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 41.9321 | 1138.2811 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 40.9918 | 1137.3408 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 39.4574 | 1135.8064 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 36.6577 | 1133.0067
[5 empty] | 344 | 1090.39 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 56.015 | 46.5371 | 56.015 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 46.5371 | 1136.9271 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 45.4401 | 1135.8301 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 43.65 | 1134.04 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 40.3837 | 1130.7737
[5 empty] | 346 | 1087.765 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 58.64 | 47.8081 | 58.64 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 47.8081 | 1135.5731 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 46.5544 | 1134.3194 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 44.5086 | 1132.2736 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 40.7756 | 1128.5406
[5 empty] | 348 | 1084.661 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 61.744 | 49.5582 | 61.744 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 49.5582 | 1134.2192 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 48.1477 | 1132.8087 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 45.8462 | 1130.5072 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 41.6466 | 1126.3076
[5 empty] | 350 | 1081.662 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 64.743 | 51.2032 | 64.743 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 51.2032 | 1132.8652 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 49.636 | 1131.298 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 47.0787 | 1128.7407 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 42.4126 | 1124.0746
[5 empty] | 352 | 1076.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 69.533 | 54.6392 | 69.533 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 54.6392 | 1131.5112 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 52.9153 | 1129.7873 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 50.1023 | 1126.9743 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 44.9695 | 1121.8415
[5 empty] | 354 | 1070.898 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 75.507 | 59.2592 | 75.507 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 59.2592 | 1130.1572 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 57.3786 | 1128.2766 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 54.3099 | 1125.2079 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 48.7105 | 1119.6085
[5 empty] | 356 | 1065.018 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 81.387 | 63.7852 | 81.387 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 63.7852 | 1128.8032 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 61.7479 | 1126.7659 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 58.4235 | 1123.4415 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 52.3574 | 1117.3754
[5 empty] | 358 | 1059.58 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 86.825 | 67.8693 | 86.825 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 67.8693 | 1127.4493 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 65.6752 | 1125.2552 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 62.095 | 1121.675 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.5624 | 1115.1424
[5 empty] | 360 | 1055.284 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 91.121 | 70.8113 | 91.121 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 70.8113 | 1126.0953 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 68.4605 | 1123.7445 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 64.6246 | 1119.9086 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 57.6253 | 1112.9093
[5 empty] | 362 | 1050.886 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 95.519 | 73.8553 | 95.519 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 73.8553 | 1124.7413 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 71.3478 | 1122.2338 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 67.2562 | 1118.1422 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 59.7903 | 1110.6763
[5 empty] | 364 | 1052.647 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 93.758 | 70.7403 | 93.758 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 70.7403 | 1123.3873 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 68.0761 | 1120.7231 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 63.7288 | 1116.3758 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.7962 | 1108.4432
[5 empty] | 366 | 1051.117 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 95.288 | 70.9163 | 95.288 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 70.9163 | 1122.0333 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 68.0954 | 1119.2124 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 63.4923 | 1114.6093 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.0932 | 1106.2102
[5 empty] | 368 | 1048.266 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 98.139 | 72.4133 | 98.139 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 72.4133 | 1120.6793 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 69.4357 | 1117.7017 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 64.5769 | 1112.8429 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.7112 | 1103.9772
[5 empty] | 370 | 1040.172 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 106.233 | 79.1534 | 106.233 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 79.1534 | 1119.3254 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 76.0191 | 1116.1911 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 70.9045 | 1111.0765 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 61.5721 | 1101.7441
[5 empty] | 372 | 1033.483 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 112.922 | 84.4884 | 112.922 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 84.4884 | 1117.9714 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 81.1974 | 1114.6804 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 75.8271 | 1109.3101 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 66.0281 | 1099.5111
[5 empty] | 374 | 1030.95 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 115.455 | 85.6674 | 115.455 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 85.6674 | 1116.6174 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 82.2197 | 1113.1697 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 76.5936 | 1107.5436 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 66.328 | 1097.278
[5 empty] | 376 | 1032.263 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 114.142 | 83.0004 | 114.142 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 83.0004 | 1115.2634 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.396 | 1111.659 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 73.5142 | 1105.7772 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 62.782 | 1095.045
[5 empty] | 378 | 1031.391 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 115.014 | 82.5184 | 115.014 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 82.5184 | 1113.9094 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 78.7573 | 1110.1483 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 72.6198 | 1104.0108 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 61.4209 | 1092.8119
[5 empty] | 380 | 1025.791 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 120.614 | 86.7645 | 120.614 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 86.7645 | 1112.5555 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 82.8466 | 1108.6376 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 76.4534 | 1102.2444 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 64.7879 | 1090.5789
[5 empty] | 382 | 1020.911 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 125.494 | 90.2905 | 125.494 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 90.2905 | 1111.2015 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 86.2159 | 1107.1269 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 79.5669 | 1100.4779 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 67.4348 | 1088.3458
[5 empty] | 384 | 1015.65 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 130.755 | 94.1975 | 130.755 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 94.1975 | 1109.8475 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 89.9662 | 1105.6162 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 83.0615 | 1098.7115 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 70.4628 | 1086.1128
[5 empty] | 386 | 1012.139 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 134.266 | 96.3545 | 134.266 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 96.3545 | 1108.4935 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 91.9665 | 1104.1055 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 84.8061 | 1096.9451 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 71.7407 | 1083.8797
[5 empty] | 388 | 1010.472 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 135.933 | 96.6675 | 135.933 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 96.6675 | 1107.1395 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 92.1228 | 1102.5948 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 84.7067 | 1095.1787 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 71.1747 | 1081.6467
[5 empty] | 390 | 1005.401 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 141.004 | 100.3845 | 141.004 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 100.3845 | 1105.7855 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 95.6831 | 1101.0841 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 88.0112 | 1093.4122 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 74.0127 | 1079.4137
[5 empty] | 392 | 996.666 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 149.739 | 107.7656 | 149.739 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 107.7656 | 1104.4316 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 102.9074 | 1099.5734 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 94.9798 | 1091.6458 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 80.5146 | 1077.1806
[5 empty] | 394 | 991.35 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 155.055 | 111.7276 | 155.055 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 111.7276 | 1103.0776 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 106.7127 | 1098.0627 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 98.5294 | 1089.8794 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 83.5976 | 1074.9476
[5 empty] | 396 | 990.486 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 155.919 | 111.2376 | 155.919 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 111.2376 | 1101.7236 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 106.066 | 1096.552 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 97.627 | 1088.113 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 82.2285 | 1072.7145
[5 empty] | 398 | 992.761 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 153.644 | 107.6086 | 153.644 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 107.6086 | 1100.3696 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 102.2803 | 1095.0413 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 93.5855 | 1086.3465 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 77.7205 | 1070.4815
[5 empty] | 400 | 999.077 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 147.328 | 99.9386 | 147.328 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 99.9386 | 1099.0156 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 94.4536 | 1093.5306 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 85.5031 | 1084.5801 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 69.1714 | 1068.2484
[5 empty] | 402 | 1001.8 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 144.605 | 95.8616 | 144.605 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 95.8616 | 1097.6616 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 90.2199 | 1092.0199 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 81.0137 | 1082.8137 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 64.2154 | 1066.0154
[5 empty] | 404 | 1002.224 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 144.181 | 94.0837 | 144.181 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 94.0837 | 1096.3077 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 88.2852 | 1090.5092 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 78.8233 | 1081.0473 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 61.5583 | 1063.7823
[5 empty] | 406 | 1002.003 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 144.402 | 92.9507 | 144.402 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.9507 | 1094.9537 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 86.9955 | 1088.9985 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 77.2778 | 1079.2808 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 59.5463 | 1061.5493
[5 empty] | 408 | 1003.596 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 142.809 | 90.0037 | 142.809 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 90.0037 | 1093.5997 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 83.8918 | 1087.4878 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 73.9184 | 1077.5144 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.7203 | 1059.3163
[5 empty] | 410 | 994.111 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 152.294 | 98.1347 | 152.294 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 98.1347 | 1092.2457 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 91.8661 | 1085.9771 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 81.637 | 1075.748 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 62.9722 | 1057.0832
[5 empty] | 412 | 983.925 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 162.48 | 106.9667 | 162.48 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 106.9667 | 1090.8917 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 100.5414 | 1084.4664 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 90.0566 | 1073.9816 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 70.9252 | 1054.8502
[5 empty] | 414 | 972.347 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 174.058 | 117.1908 | 174.058 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 117.1908 | 1089.5378 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 110.6087 | 1082.9557 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 99.8681 | 1072.2151 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 80.2701 | 1052.6171
[5 empty] | 416 | 963.901 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 182.504 | 124.2828 | 182.504 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 124.2828 | 1088.1838 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 117.544 | 1081.445 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 106.5477 | 1070.4487 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 86.4831 | 1050.3841
[5 empty] | 418 | 963.258 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.147 | 123.5718 | 183.147 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 123.5718 | 1086.8298 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 116.6763 | 1079.9343 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 105.4243 | 1068.6823 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 84.893 | 1048.151
[5 empty] | 420 | 965.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.533 | 119.6038 | 180.533 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 119.6038 | 1085.4758 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 112.5516 | 1078.4236 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 101.0439 | 1066.9159 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 80.046 | 1045.918
[5 empty] | 422 | 966.177 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.228 | 117.9448 | 180.228 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 117.9448 | 1084.1218 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 110.7359 | 1076.9129 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 98.9724 | 1065.1494 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 77.5079 | 1043.6849
[5 empty] | 424 | 973.825 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 172.58 | 108.9428 | 172.58 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 108.9428 | 1082.7678 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 101.5772 | 1075.4022 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 89.558 | 1063.383 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 67.6269 | 1041.4519
[5 empty] | 426 | 983.972 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 162.433 | 97.4419 | 162.433 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 97.4419 | 1081.4139 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 89.9195 | 1073.8915 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 77.6446 | 1061.6166 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.2469 | 1039.2189
[5 empty] | 428 | 994.096 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 152.309 | 85.9639 | 152.309 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 85.9639 | 1080.0599 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 78.2848 | 1072.3808 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 65.7542 | 1059.8502 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 42.8898 | 1036.9858
[5 empty] | 430 | 991.695 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 154.71 | 87.0109 | 154.71 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 87.0109 | 1078.7059 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.1751 | 1070.8701 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 66.3887 | 1058.0837 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 43.0578 | 1034.7528
[5 empty] | 432 | 984.933 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 161.472 | 92.4189 | 161.472 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.4189 | 1077.3519 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 84.4264 | 1069.3594 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 71.3843 | 1056.3173 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 47.5867 | 1032.5197
[5 empty] | 434 | 974.509 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 171.896 | 101.4889 | 171.896 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 101.4889 | 1075.9979 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 93.3397 | 1067.8487 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 80.0419 | 1054.5509 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.7777 | 1030.2867
[5 empty] | 436 | 966.698 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 179.707 | 107.946 | 179.707 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 107.946 | 1074.644 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 99.64 | 1066.338 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 86.0865 | 1052.7845 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 61.3556 | 1028.0536
[5 empty] | 438 | 963.618 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 182.787 | 109.672 | 182.787 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 109.672 | 1073.29 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 101.2093 | 1064.8273 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 87.4 | 1051.018 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 62.2026 | 1025.8206
[5 empty] | 440 | 957.803 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 188.602 | 114.133 | 188.602 | 11.3161 | 998345.0349 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 114.133 | 1071.936 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 105.5136 | 1063.3166 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 91.4486 | 1049.2516 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 65.7845 | 1023.5875
[5 empty] | 442 | 954.277 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 192.128 | 116.305 | 192.128 | 11.5277 | 1016889.2597 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 116.305 | 1070.582 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 107.5289 | 1061.8059 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 93.2082 | 1047.4852 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 67.0775 | 1021.3545
[5 empty] | 444 | 947.182 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 199.223 | 122.046 | 199.223 | 11.9534 | 1054190.4781 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 122.046 | 1069.228 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 113.1132 | 1060.2952 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 98.5368 | 1045.7188 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 71.9395 | 1019.1215
[5 empty] | 446 | 938.045 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 208.36 | 129.829 | 208.36 | 12.5016 | 1102200.9626 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 129.829 | 1067.874 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 120.7395 | 1058.7845 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 105.9073 | 1043.9523 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 78.8434 | 1016.8884
[5 empty] | 448 | 930.871 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 215.534 | 135.6491 | 215.534 | 12.932 | 1139876.0607 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 135.6491 | 1066.5201 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 126.4028 | 1057.2738 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 111.3149 | 1042.1859 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 83.7844 | 1014.6554
[5 empty] | 450 | 926.391 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 220.014 | 138.7751 | 220.014 | 13.2008 | 1163394.033 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 138.7751 | 1065.1661 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 129.3722 | 1055.7632 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 114.0285 | 1040.4195 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 86.0313 | 1012.4223
[5 empty] | 452 | 918.344 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 228.061 | 145.4681 | 228.061 | 13.6837 | 1205619.2415 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 145.4681 | 1063.8121 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 135.9085 | 1054.2525 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 120.3091 | 1038.6531 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 91.8453 | 1010.1893
[5 empty] | 454 | 911.505 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 234.9 | 150.9531 | 234.9 | 14.094 | 1241487.607 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 150.9531 | 1062.4581 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 141.2368 | 1052.7418 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 125.3816 | 1036.8866 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 96.4512 | 1007.9562
[5 empty] | 456 | 903.61 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 242.795 | 157.4941 | 242.795 | 14.5677 | 1282873.6994 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 157.4941 | 1061.1041 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 147.6211 | 1051.2311 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 131.5102 | 1035.1202 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 102.1132 | 1005.7232
[5 empty] | 458 | 900.63 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 245.775 | 159.1202 | 245.775 | 14.7465 | 1298489.2946 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 159.1202 | 1059.7502 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 149.0904 | 1049.7204 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 132.7238 | 1033.3538 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 102.8601 | 1003.4901
[5 empty] | 460 | 904.066 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 242.339 | 154.3302 | 242.339 | 14.5403 | 1280483.9207 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 154.3302 | 1058.3962 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 144.1437 | 1048.2097 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 127.5214 | 1031.5874 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 97.1911 | 1001.2571
[5 empty] | 462 | 915.092 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 231.313 | 141.9502 | 231.313 | 13.8788 | 1222677.0116 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 141.9502 | 1057.0422 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 131.607 | 1046.699 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 114.7289 | 1029.8209 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 83.932 | 999.024
[5 empty] | 464 | 905.556 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 240.849 | 150.1322 | 240.849 | 14.4509 | 1272674.6991 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 150.1322 | 1055.6882 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 139.6323 | 1045.1883 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 122.4985 | 1028.0545 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 91.235 | 996.791
[5 empty] | 466 | 905.271 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 241.134 | 149.0632 | 241.134 | 14.468 | 1274168.4703 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 149.0632 | 1054.3342 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 138.4066 | 1043.6776 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 121.0171 | 1026.2881 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 89.287 | 994.558
[5 empty] | 468 | 901.918 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 244.487 | 151.0622 | 244.487 | 14.6692 | 1291740.3907 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 151.0622 | 1052.9802 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 140.2489 | 1042.1669 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 122.6037 | 1024.5217 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 90.4069 | 992.3249
[5 empty] | 470 | 895.651 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 250.754 | 155.9753 | 250.754 | 15.0452 | 1324572.8786 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 155.9753 | 1051.6263 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 145.0052 | 1040.6562 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 127.1042 | 1022.7552 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 94.4409 | 990.0919
[5 empty] | 472 | 892.304 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 254.101 | 157.9683 | 254.101 | 15.2461 | 1342101.9243 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 157.9683 | 1050.2723 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 146.8415 | 1039.1455 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 128.6848 | 1020.9888 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 95.5548 | 987.8588
[5 empty] | 474 | 895.279 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 251.126 | 153.6393 | 251.126 | 15.0676 | 1326521.3288 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 153.6393 | 1048.9183 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 142.3558 | 1037.6348 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 123.9434 | 1019.2224 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 90.3468 | 985.6258
[5 empty] | 476 | 896.818 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 249.587 | 150.7463 | 249.587 | 14.9752 | 1318460.0829 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 150.7463 | 1047.5643 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 139.3061 | 1036.1241 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 120.638 | 1017.456 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 86.5747 | 983.3927
[5 empty] | 478 | 909.921 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 236.484 | 136.2893 | 236.484 | 14.189 | 1249792.8108 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 136.2893 | 1046.2103 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 124.6924 | 1034.6134 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 105.7685 | 1015.6895 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 71.2387 | 981.1597
[5 empty] | 480 | 926.295 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 220.11 | 118.5614 | 220.11 | 13.2066 | 1163897.9115 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 118.5614 | 1044.8564 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 106.8077 | 1033.1027 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 87.6281 | 1013.9231 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 52.6316 | 978.9266
[5 empty] | 482 | 924.888 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 221.517 | 116.5357 | 221.517 | 11.0758 | 813390.6291 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 116.5357 | 1041.4237 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 104.3737 | 1029.2617 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 84.5255 | 1009.4135 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 48.2967 | 973.1847
[5 empty] | 484 | 919.044 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 227.361 | 118.9471 | 227.361 | 11.368 | 834685.4365 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 118.9471 | 1037.9911 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 106.3767 | 1025.4207 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 85.8599 | 1004.9039 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 48.3988 | 967.4428
[5 empty] | 486 | 911.164 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 235.241 | 123.3945 | 235.241 | 11.7621 | 863385.8389 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 123.3945 | 1034.5585 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 110.4158 | 1021.5798 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 89.2303 | 1000.3943 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 50.5368 | 961.7008
[5 empty] | 488 | 903.893 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 242.512 | 127.2329 | 242.512 | 12.1256 | 889854.568 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 127.2329 | 1031.1259 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 113.8458 | 1017.7388 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 91.9916 | 995.8846 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 52.0659 | 955.9589
[5 empty] | 490 | 901.953 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 244.452 | 125.7403 | 244.452 | 12.2226 | 896914.5753 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 125.7403 | 1027.6933 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 111.9448 | 1013.8978 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 89.422 | 991.375 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 48.264 | 950.217
[5 empty] | 492 | 900.198 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 246.207 | 124.0627 | 246.207 | 12.3103 | 903300.5349 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 124.0627 | 1024.2607 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 109.8588 | 1010.0568 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 86.6674 | 986.8654 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 44.277 | 944.475
[5 empty] | 494 | 904.177 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 242.228 | 116.6511 | 242.228 | 12.1114 | 888820.9632 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 116.6511 | 1020.8281 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 102.0389 | 1006.2159 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 78.1788 | 982.3558 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 34.5561 | 938.7331
[5 empty] | 496 | 912.253 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 234.152 | 105.1425 | 234.152 | 11.7076 | 859420.4135 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 105.1425 | 1017.3955 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 90.1219 | 1002.3749 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 65.5932 | 977.8462 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 20.7382 | 932.9912
[5 empty] | 498 | 915.297 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 231.108 | 98.6659 | 231.108 | 11.5554 | 848334.606 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 98.6659 | 1013.9629 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 83.2369 | 998.5339 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 58.0395 | 973.3365 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 11.9522 | 927.2492
|  |  |  | Reservoir | 500 | 919.629 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 10 | 10 | 10 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 10 | 929.629 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 10 | 929.629 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 10 | 929.629 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 10 | 929.629
[15 empty] | Total Steel Mass (kg): | 401514097.3514