## Cost Estimates
Air Valve, Scour Valve & Isolating Budget |  |  |  | Steel Pipe Prices |  | Pump Station Costs - DWA 2003 Escalated to 2010 |  | Electricity Costs | Pula | Rand | Reservoir Costing |  | Minor Loss - k | 150 | Pipe Trench Excavation & Back Fill
Pipe Diameter (mm) | Civil Rate/m | Mechanical Rate/m | Total R/m | Coating Cost Per m2 | 200 | PS Capacity kW | Cost R/kW | Fixed Charge Per Month | 26.09 | 28.699 | Reservoir (incl. earthowrks and lining) per m3 | 80 |  |  | Excavation Cost (R/m3) | 50
500 | 40 | 70 | 110 | Steel Pipe Cost Per Ton | 17.5 | 100 | 30227.6622 | Energy Charge Per kWh | 0.4096 | 0.45056 |  |  | Friction Factors |  | Bedding and Cradle Fill (R/m3) | 165
600 | 40 | 80 | 120 | Delivery Cost Per m | 85 | 200 | 25032.9622 | [5 empty] | Ks (mm) - New | 0.03 | Main Fill (R/m3) | 55
700 | 40 | 100 | 140 | Laying and Joining 20% of Pipe Price |  | 300 | 22423.6676 | [5 empty] | Ks (mm) - Average | 0.06 | Spoil (R/m3) | 45
800 | 40 | 140 | 180 |  |  | 400 | 20740.1478 | [5 empty] | Ks (mm) - Old | 0.15
900 | 40 | 190 | 230 |  |  | 500 | 19523.2464 | [5 empty] | Ks (mm) - Biofilm | 0.5
1000 | 40 | 250 | 290 |  |  | 600 | 18582.6012
1100 | 40 | 360 | 400 |  |  | 700 | 17823.054
1200 | 50 | 460 | 510 |  |  | 800 | 17190.3824
1300 | 50 | 480 | 530 |  |  | 900 | 16651.2418
1400 | 50 | 500 | 550 |  |  | 1000 | 16183.5318
1500 | 50 | 530 | 580 |  |  | 2000 | 13420.2993
1600 | 60 | 560 | 620 |  |  | 3000 | 12030.295
1700 | 60 | 580 | 640 |  |  | 5000 | 10484.1624
1800 | 60 | 600 | 660 |  |  | 6000 | 9982.2899
1900 | 70 | 640 | 710 |  |  | 7000 | 9576.9667
2000 | 70 | 680 | 750 |  |  | 8000 | 9239.3348
2100 | 70 | 720 | 790 |  |  | 9000 | 8951.5188
2200 | 80 | 760 | 840 |  |  | 10000 | 8701.7305
2300 | 80 | 770 | 850 |  |  | 20000 | 7225.0136
2400 | 90 | 810 | 900 |  |  | 40000 | 6001.0824
2500 | 90 | 850 | 940 |  |  | 50000 | 5653.4377
[6 empty] | 60000 | 5384.5442
[6 empty] | 70000 | 5167.2937
[6 empty] | 80000 | 4986.2759
[6 empty] | 90000 | 4831.929
[6 empty] | 100000 | 4697.9511

## Pipeline Pricing
Option 4B Pipeline Pricing
Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Pipe Wall thickness (mm) | Steel Mass (kg) | Pipe Area (m2) | Coating Cost | Delivery Cost | Pipe Cost | Chamber Cost R/m | Chamber Cost R | Pumpstation Name | Pump Station Power | Reservoir Name | Volume m3
2 | 1069.018 | 0 | 1.9 | 11.875 | 0 | 0 | 0 | 0 | 0 | 710 | 0 | PS1 | 2342 | BPT 3 | 35277.12
4 | 1067.321 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000 | PS3 | 12177 | BPT 5 | 35277.12
6 | 1064.035 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
8 | 1063.832 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
10 | 1067.893 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
12 | 1075.133 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
14 | 1082.768 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
16 | 1089.726 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
18 | 1094.131 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
20 | 1097.897 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
22 | 1101.67 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
24 | 1095.952 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
26 | 1090.107 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
28 | 1085.781 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
30 | 1081.89 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
32 | 1077.937 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
34 | 1074.89 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
36 | 1071.114 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
38 | 1065.311 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
40 | 1059.051 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
42 | 1054.28 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
44 | 1053.871 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
46 | 1050.42 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
48 | 1052.704 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
50 | 1056.355 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
52 | 1058.466 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
54 | 1055.99 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
56 | 1055.66 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
58 | 1056.404 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
60 | 1056.841 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
62 | 1056.377 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
64 | 1052.503 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
66 | 1046.022 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
68 | 1036.575 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
70 | 1031.818 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
72 | 1027.675 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
74 | 1023.844 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
76 | 1020.888 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
78 | 1023.648 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
80 | 1027.566 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
82 | 1032.371 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
84 | 1034.983 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
86 | 1033.213 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
88 | 1031.188 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
90 | 1029.08 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
92 | 1026.322 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
94 | 1023.207 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
96 | 1021.503 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
98 | 1019.765 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
100 | 1018.493 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
102 | 1016.444 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
104 | 1013.288 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
106 | 1007.843 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
108 | 1001.282 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
110 | 996.609 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
112 | 992.999 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
114 | 993.639 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
116 | 994.611 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
118 | 995.751 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
120 | 996.479 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
122 | 996.147 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
124 | 992.094 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
126 | 985.623 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
128 | 977.759 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
130 | 969.772 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
132 | 981.785 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
134 | 991.458 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
136 | 987.77 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
138 | 982.725 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
140 | 977.559 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
142 | 975.289 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
144 | 973.968 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
146 | 962.473 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
148 | 951.285 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
150 | 948.174 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
152 | 944.641 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
154 | 941.566 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
156 | 940.942 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
158 | 939.726 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
160 | 936.738 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
162 | 933.65 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
164 | 932.745 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
166 | 931.696 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
168 | 930.999 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
170 | 930.885 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
172 | 930.378 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
174 | 931.324 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
176 | 933.53 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
178 | 932.714 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
180 | 928.311 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
182 | 924.179 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
184 | 928.398 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
186 | 930.866 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
188 | 928.411 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
190 | 927.849 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
192 | 926.71 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
194 | 926.201 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
196 | 924.509 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
198 | 923.417 | 2 | 1.8 | 11.2952 | 996509.3057 | 11309.7336 | 2261946.7106 | 170000 | 17438912.8492 | 660 | 1320000
200 | 923.011 | 2 | 1.8 | 11.3195 | 998644.849 | 11309.7336 | 2261946.7106 | 170000 | 17476284.8575 | 660 | 1320000
202 | 921.969 | 2 | 1.8 | 11.3821 | 1004125.4583 | 11309.7336 | 2261946.7106 | 170000 | 17572195.5205 | 660 | 1320000
204 | 920.661 | 2 | 1.8 | 11.4605 | 1011004.6025 | 11309.7336 | 2261946.7106 | 170000 | 17692580.5441 | 660 | 1320000
206 | 920.243 | 2 | 1.8 | 11.4856 | 1013202.8554 | 11309.7336 | 2261946.7106 | 170000 | 17731049.9688 | 660 | 1320000
208 | 919.297 | 2 | 1.8 | 11.5424 | 1018177.6195 | 11309.7336 | 2261946.7106 | 170000 | 17818108.3416 | 660 | 1320000
210 | 917.533 | 2 | 1.8 | 11.6482 | 1027453.1808 | 11309.7336 | 2261946.7106 | 170000 | 17980430.6641 | 660 | 1320000
212 | 917.684 | 2 | 1.8 | 11.6392 | 1026659.2276 | 11309.7336 | 2261946.7106 | 170000 | 17966536.4829 | 660 | 1320000
214 | 915.724 | 2 | 1.8 | 11.7568 | 1036964.2159 | 11309.7336 | 2261946.7106 | 170000 | 18146873.7777 | 660 | 1320000
216 | 915.73 | 2 | 1.8 | 11.7564 | 1036932.6721 | 11309.7336 | 2261946.7106 | 170000 | 18146321.7612 | 660 | 1320000
218 | 915.584 | 2 | 1.8 | 11.7652 | 1037700.2343 | 11309.7336 | 2261946.7106 | 170000 | 18159754.0995 | 660 | 1320000
220 | 915.444 | 2 | 1.8 | 11.7736 | 1038436.2457 | 11309.7336 | 2261946.7106 | 170000 | 18172634.2995 | 660 | 1320000
222 | 913.52 | 2 | 1.8 | 11.889 | 1048550.4405 | 11309.7336 | 2261946.7106 | 170000 | 18349632.708 | 660 | 1320000
224 | 912.524 | 2 | 1.8 | 11.9488 | 1053785.7546 | 11309.7336 | 2261946.7106 | 170000 | 18441250.7056 | 660 | 1320000
226 | 912.565 | 2 | 1.8 | 11.9463 | 1053570.2516 | 11309.7336 | 2261946.7106 | 170000 | 18437479.4037 | 660 | 1320000
228 | 913.484 | 2 | 2.2 | 19.8 | 2129173.4923 | 13823.0077 | 2764601.5352 | 170000 | 37260536.1153 | 840 | 1680000
230 | 913.545 | 2 | 2.2 | 19.7557 | 2124456.501 | 13823.0077 | 2764601.5352 | 170000 | 37177988.7682 | 840 | 1680000
232 | 914.546 | 2 | 2.2 | 19.6425 | 2112393.122 | 13823.0077 | 2764601.5352 | 170000 | 36966879.6348 | 840 | 1680000
234 | 918.285 | 2 | 2.2 | 19.3285 | 2078925.8204 | 13823.0077 | 2764601.5352 | 170000 | 36381201.8564 | 840 | 1680000
236 | 919.357 | 2 | 2.2 | 19.2101 | 2066302.5605 | 13823.0077 | 2764601.5352 | 170000 | 36160294.8083 | 840 | 1680000
238 | 918.649 | 2 | 2.2 | 19.2223 | 2067595.4923 | 13823.0077 | 2764601.5352 | 170000 | 36182921.1155 | 840 | 1680000
240 | 922.974 | 2 | 2.2 | 18.8653 | 2029532.1749 | 13823.0077 | 2764601.5352 | 170000 | 35516813.0608 | 840 | 1680000
242 | 927.375 | 2 | 2.2 | 18.5028 | 1990861.6963 | 13823.0077 | 2764601.5352 | 170000 | 34840079.6856 | 840 | 1680000
244 | 929.253 | 2 | 2.2 | 18.3253 | 1971922.111 | 13823.0077 | 2764601.5352 | 170000 | 34508636.942 | 840 | 1680000
246 | 930.863 | 2 | 2.2 | 18.1674 | 1955076.8099 | 13823.0077 | 2764601.5352 | 170000 | 34213844.173 | 840 | 1680000
248 | 931.924 | 2 | 2.2 | 18.0498 | 1942526.0831 | 13823.0077 | 2764601.5352 | 170000 | 33994206.4544 | 840 | 1680000
250 | 936.722 | 2 | 2.2 | 17.6582 | 1900718.089 | 13823.0077 | 2764601.5352 | 170000 | 33262566.5584 | 840 | 1680000
252 | 941.777 | 2 | 2.2 | 17.2477 | 1856881.9842 | 13823.0077 | 2764601.5352 | 170000 | 32495434.7233 | 840 | 1680000
254 | 948.143 | 2 | 2.2 | 16.741 | 1802756.2719 | 13823.0077 | 2764601.5352 | 170000 | 31548234.7585 | 840 | 1680000
256 | 955.417 | 2 | 2.2 | 16.1678 | 1741486.2968 | 13823.0077 | 2764601.5352 | 170000 | 30476010.1934 | 840 | 1680000
258 | 962.7 | 2 | 2.2 | 15.5939 | 1680113.3067 | 13823.0077 | 2764601.5352 | 170000 | 29401982.8678 | 840 | 1680000
260 | 969.281 | 2 | 2.2 | 15.0715 | 1624217.5481 | 13823.0077 | 2764601.5352 | 170000 | 28423807.0909 | 840 | 1680000
262 | 980.284 | 2 | 2.2 | 14.2249 | 1533567.2726 | 13823.0077 | 2764601.5352 | 170000 | 26837427.2702 | 840 | 1680000
264 | 986.551 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
266 | 989.198 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
268 | 994.39 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
270 | 999.917 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
272 | 1004.623 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
274 | 1008.819 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
276 | 1007.834 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
278 | 1005.626 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
280 | 1001.623 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
282 | 1004.052 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
284 | 1010.797 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
286 | 1014.67 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
288 | 1017.319 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
290 | 1027.459 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
292 | 1031.99 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
294 | 1036.254 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
296 | 1040.127 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
298 | 1044.396 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
300 | 1051.339 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
302 | 1060.955 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
304 | 1070.227 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
306 | 1072.691 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
308 | 1076.503 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
310 | 1083.996 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
312 | 1097.188 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
314 | 1103.545 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
316 | 1105.174 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
318 | 1111.657 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
320 | 1122.935 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
322 | 1128.197 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
324 | 1132.561 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
326 | 1131.854 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
328 | 1133.338 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
330 | 1136.405 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
332 | 1128.709 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
334 | 1120.713 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
336 | 1115.226 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
338 | 1108.709 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
340 | 1102.499 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
342 | 1096.349 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
344 | 1090.39 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
346 | 1087.765 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
348 | 1084.661 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
350 | 1081.662 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
352 | 1076.872 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
354 | 1070.898 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
356 | 1065.018 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
358 | 1059.58 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
360 | 1055.284 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
362 | 1050.886 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
364 | 1052.647 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
366 | 1051.117 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
368 | 1048.266 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
370 | 1040.172 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
372 | 1033.483 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
374 | 1030.95 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
376 | 1032.263 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
378 | 1031.391 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
380 | 1025.791 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
382 | 1020.911 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
384 | 1015.65 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
386 | 1012.139 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
388 | 1010.472 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
390 | 1005.401 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
392 | 996.666 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
394 | 991.35 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
396 | 990.486 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
398 | 992.761 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
400 | 999.077 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
402 | 1001.8 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
404 | 1002.224 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
406 | 1002.003 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
408 | 1003.596 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
410 | 994.111 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
412 | 983.925 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
414 | 972.347 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
416 | 963.901 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
418 | 963.258 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
420 | 965.872 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
422 | 966.177 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
424 | 973.825 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
426 | 983.972 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
428 | 994.096 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
430 | 991.695 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
432 | 984.933 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
434 | 974.509 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
436 | 966.698 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
438 | 963.618 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
440 | 957.803 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
442 | 954.277 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
444 | 947.182 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
446 | 938.045 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
448 | 930.871 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
450 | 926.391 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
452 | 918.344 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
454 | 911.505 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
456 | 903.61 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
458 | 900.63 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
460 | 904.066 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
462 | 915.092 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
464 | 905.556 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
466 | 905.271 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
468 | 901.918 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
470 | 895.651 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
472 | 892.304 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
474 | 895.279 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
476 | 896.818 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
478 | 909.921 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
480 | 926.295 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
482 | 924.888 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
484 | 919.044 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
486 | 911.164 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
488 | 903.893 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
490 | 901.953 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
492 | 900.198 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
494 | 904.177 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
496 | 912.253 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
498 | 915.297 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000
500 | 919.629 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000

## Pipeline Instalation Costs
Option 4B Excavation and Back Fill Pricing
Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Trench Width (m) | Trench Depth (m) | Excavation (m3) | Bedding and Cradle Fill (m3) | Main fill (m3) | Spoil (m3) | Excavation Cost | Bedding and Cradle Fill Cost | Main Fill Cost | Spoil Cost
2 | 1069.018 | 0 | 1.9 | 2.9 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1067.321 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
6 | 1064.035 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
8 | 1063.832 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
10 | 1067.893 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
12 | 1075.133 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
14 | 1082.768 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
16 | 1089.726 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
18 | 1094.131 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
20 | 1097.897 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
22 | 1101.67 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
24 | 1095.952 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
26 | 1090.107 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
28 | 1085.781 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
30 | 1081.89 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
32 | 1077.937 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
34 | 1074.89 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
36 | 1071.114 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
38 | 1065.311 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
40 | 1059.051 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
42 | 1054.28 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
44 | 1053.871 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
46 | 1050.42 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
48 | 1052.704 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
50 | 1056.355 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
52 | 1058.466 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
54 | 1055.99 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
56 | 1055.66 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
58 | 1056.404 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
60 | 1056.841 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
62 | 1056.377 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
64 | 1052.503 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
66 | 1046.022 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
68 | 1036.575 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
70 | 1031.818 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
72 | 1027.675 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
74 | 1023.844 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
76 | 1020.888 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
78 | 1023.648 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
80 | 1027.566 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
82 | 1032.371 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
84 | 1034.983 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
86 | 1033.213 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
88 | 1031.188 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
90 | 1029.08 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
92 | 1026.322 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
94 | 1023.207 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
96 | 1021.503 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
98 | 1019.765 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
100 | 1018.493 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
102 | 1016.444 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
104 | 1013.288 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
106 | 1007.843 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
108 | 1001.282 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
110 | 996.609 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
112 | 992.999 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
114 | 993.639 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
116 | 994.611 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
118 | 995.751 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
120 | 996.479 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
122 | 996.147 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
124 | 992.094 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
126 | 985.623 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
128 | 977.759 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
130 | 969.772 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
132 | 981.785 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
134 | 991.458 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
136 | 987.77 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
138 | 982.725 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
140 | 977.559 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
142 | 975.289 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
144 | 973.968 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
146 | 962.473 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
148 | 951.285 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
150 | 948.174 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
152 | 944.641 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
154 | 941.566 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
156 | 940.942 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
158 | 939.726 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
160 | 936.738 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
162 | 933.65 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
164 | 932.745 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
166 | 931.696 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
168 | 930.999 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
170 | 930.885 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
172 | 930.378 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
174 | 931.324 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
176 | 933.53 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
178 | 932.714 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
180 | 928.311 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
182 | 924.179 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
184 | 928.398 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
186 | 930.866 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
188 | 928.411 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
190 | 927.849 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
192 | 926.71 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
194 | 926.201 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
196 | 924.509 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
198 | 923.417 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
200 | 923.011 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
202 | 921.969 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
204 | 920.661 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
206 | 920.243 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
208 | 919.297 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
210 | 917.533 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
212 | 917.684 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
214 | 915.724 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
216 | 915.73 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
218 | 915.584 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
220 | 915.444 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
222 | 913.52 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
224 | 912.524 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
226 | 912.565 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
228 | 913.484 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
230 | 913.545 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
232 | 914.546 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
234 | 918.285 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
236 | 919.357 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
238 | 918.649 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
240 | 922.974 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
242 | 927.375 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
244 | 929.253 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
246 | 930.863 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
248 | 931.924 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
250 | 936.722 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
252 | 941.777 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
254 | 948.143 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
256 | 955.417 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
258 | 962.7 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
260 | 969.281 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
262 | 980.284 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
264 | 986.551 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
266 | 989.198 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
268 | 994.39 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
270 | 999.917 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
272 | 1004.623 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
274 | 1008.819 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
276 | 1007.834 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
278 | 1005.626 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
280 | 1001.623 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
282 | 1004.052 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
284 | 1010.797 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
286 | 1014.67 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
288 | 1017.319 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
290 | 1027.459 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
292 | 1031.99 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
294 | 1036.254 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
296 | 1040.127 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
298 | 1044.396 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
300 | 1051.339 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
302 | 1060.955 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
304 | 1070.227 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
306 | 1072.691 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
308 | 1076.503 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
310 | 1083.996 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
312 | 1097.188 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
314 | 1103.545 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
316 | 1105.174 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
318 | 1111.657 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
320 | 1122.935 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
322 | 1128.197 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
324 | 1132.561 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
326 | 1131.854 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
328 | 1133.338 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
330 | 1136.405 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
332 | 1128.709 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
334 | 1120.713 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
336 | 1115.226 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
338 | 1108.709 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
340 | 1102.499 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
342 | 1096.349 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
344 | 1090.39 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
346 | 1087.765 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
348 | 1084.661 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
350 | 1081.662 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
352 | 1076.872 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
354 | 1070.898 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
356 | 1065.018 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
358 | 1059.58 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
360 | 1055.284 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
362 | 1050.886 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
364 | 1052.647 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
366 | 1051.117 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
368 | 1048.266 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
370 | 1040.172 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
372 | 1033.483 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
374 | 1030.95 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
376 | 1032.263 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
378 | 1031.391 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
380 | 1025.791 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
382 | 1020.911 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
384 | 1015.65 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
386 | 1012.139 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
388 | 1010.472 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
390 | 1005.401 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
392 | 996.666 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
394 | 991.35 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
396 | 990.486 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
398 | 992.761 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
400 | 999.077 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
402 | 1001.8 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
404 | 1002.224 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
406 | 1002.003 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
408 | 1003.596 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
410 | 994.111 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
412 | 983.925 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
414 | 972.347 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
416 | 963.901 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
418 | 963.258 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
420 | 965.872 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
422 | 966.177 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
424 | 973.825 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
426 | 983.972 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
428 | 994.096 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
430 | 991.695 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
432 | 984.933 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
434 | 974.509 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
436 | 966.698 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
438 | 963.618 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
440 | 957.803 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
442 | 954.277 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
444 | 947.182 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
446 | 938.045 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
448 | 930.871 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
450 | 926.391 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
452 | 918.344 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
454 | 911.505 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
456 | 903.61 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
458 | 900.63 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
460 | 904.066 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
462 | 915.092 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
464 | 905.556 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
466 | 905.271 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
468 | 901.918 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
470 | 895.651 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
472 | 892.304 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
474 | 895.279 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
476 | 896.818 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
478 | 909.921 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
480 | 926.295 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
482 | 924.888 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
484 | 919.044 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
486 | 911.164 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
488 | 903.893 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
490 | 901.953 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
492 | 900.198 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
494 | 904.177 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
496 | 912.253 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
498 | 915.297 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
500 | 919.629 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281

## Capital Costs
Option 4B Capital Costs
Pipe Cost | 5664810228.1407
Pipe Laying and Joining | 1132962045.6281
Pipe Trench Excavation & Back Fill | 806812851.7357
Air Valve, Scour Valve & Isolating Cost | 354000000
Pump Station Cost PS 1 | 31430340.9711
Pump Station Cost PS 3 | 105960972.005
Reservoir Cost BPT 3 | 2822169.6
Reservoir Cost BPT 5 | 2822169.6
Option 4B Capital Costs (Pula)
Pipe Cost | 5149827480.1279
Pipe Laying and Joining | 1029965496.0256
Pipe Trench Excavation & Back Fill | 733466228.8506
Air Valve, Scour Valve & Isolating Cost | 321818181.8182
Pump Station Cost PS 1 | 28573037.2465
Pump Station Cost PS 3 | 96328156.3682
Reservoir Cost BPT 3 | 2565608.7273
Reservoir Cost BPT 5 | 2565608.7273

## Maintenance Costs
Option 8 Maintenance Costs
Item | Percentage Per Annum | Cost R/year
Civil | 0.5% | 28352272.8367
Mechanical & Electrical | 4% | 19655652.519
Total |  | 48007925.3558
Option 8 Maintenance Costs (Pula)
Item | Percentage Per Annum | Cost P/year
Civil | 0.5% | 25774793.4879
Mechanical & Electrical | 4% | 17868775.0173
Total |  | 43643568.5052

## Pumping Costs Calculation
Option 8 Pumping Costs Calculations -PS 1
Pipeline Details |  |  |  | New Pipe Flow Equation |  |  | Average Pipe Flow Equation |  |  | Old Pipe Flow Equation |  |  | Biofilm Pipe Flow Equation
Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component
2 | 1069.018 | 0 | 1.9 | 0.00867 | 0 | 0 | 0.0097304 | 0 | 0 | 0.011459 | 0 | 0 | 0.014543 | 0 | 0
4 | 1067.321 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042
6 | 1064.035 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042
8 | 1063.832 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042
10 | 1067.893 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042
12 | 1075.133 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042
14 | 1082.768 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042
16 | 1089.726 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042
18 | 1094.131 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042
20 | 1097.897 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042
22 | 1101.67 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
Option 8 Pumping Costs Calculations - PS 3
Pipeline Details |  |  |  | New Pipe Flow Equation |  |  | Average Pipe Flow Equation |  |  | Old Pipe Flow Equation |  |  | Biofilm Pipe Flow Equation
Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component
228 | 913.484 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
230 | 913.545 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
232 | 914.546 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
234 | 918.285 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
236 | 919.357 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
238 | 918.649 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
240 | 922.974 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
242 | 927.375 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
244 | 929.253 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
246 | 930.863 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
248 | 931.924 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
250 | 936.722 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
252 | 941.777 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
254 | 948.143 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
256 | 955.417 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
258 | 962.7 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
260 | 969.281 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
262 | 980.284 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
264 | 986.551 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
266 | 989.198 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
268 | 994.39 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
270 | 999.917 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
272 | 1004.623 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
274 | 1008.819 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
276 | 1007.834 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
278 | 1005.626 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
280 | 1001.623 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
282 | 1004.052 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
284 | 1010.797 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
286 | 1014.67 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
288 | 1017.319 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
290 | 1027.459 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
292 | 1031.99 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
294 | 1036.254 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
296 | 1040.127 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
298 | 1044.396 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
300 | 1051.339 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
302 | 1060.955 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
304 | 1070.227 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
306 | 1072.691 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
308 | 1076.503 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
310 | 1083.996 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
312 | 1097.188 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
314 | 1103.545 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
316 | 1105.174 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
318 | 1111.657 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
320 | 1122.935 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
322 | 1128.197 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
324 | 1132.561 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
326 | 1131.854 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
328 | 1133.338 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
330 | 1136.405 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
332 | 1128.709 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
334 | 1120.713 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
336 | 1115.226 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
338 | 1108.709 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
340 | 1102.499 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
342 | 1096.349 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
344 | 1090.39 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
346 | 1087.765 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
348 | 1084.661 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
350 | 1081.662 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
352 | 1076.872 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
354 | 1070.898 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
356 | 1065.018 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
358 | 1059.58 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
360 | 1055.284 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
362 | 1050.886 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
364 | 1052.647 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
366 | 1051.117 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
368 | 1048.266 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
370 | 1040.172 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
372 | 1033.483 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
374 | 1030.95 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
376 | 1032.263 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
378 | 1031.391 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
380 | 1025.791 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
382 | 1020.911 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
384 | 1015.65 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
386 | 1012.139 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
388 | 1010.472 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
390 | 1005.401 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
392 | 996.666 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
394 | 991.35 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
396 | 990.486 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
398 | 992.761 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
400 | 999.077 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
402 | 1001.8 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
404 | 1002.224 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
406 | 1002.003 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
408 | 1003.596 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
410 | 994.111 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
412 | 983.925 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
414 | 972.347 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
416 | 963.901 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
418 | 963.258 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
420 | 965.872 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
422 | 966.177 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
424 | 973.825 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
426 | 983.972 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
428 | 994.096 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
430 | 991.695 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
432 | 984.933 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
434 | 974.509 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
436 | 966.698 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
438 | 963.618 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
440 | 957.803 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
442 | 954.277 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
444 | 947.182 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
446 | 938.045 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
448 | 930.871 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
450 | 926.391 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
452 | 918.344 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
454 | 911.505 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
456 | 903.61 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
458 | 900.63 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
460 | 904.066 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
462 | 915.092 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
464 | 905.556 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
466 | 905.271 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
468 | 901.918 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
470 | 895.651 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
472 | 892.304 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
474 | 895.279 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
476 | 896.818 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
478 | 909.921 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
480 | 926.295 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
482 | 924.888 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
484 | 919.044 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
486 | 911.164 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
488 | 903.893 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
490 | 901.953 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
492 | 900.198 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
494 | 904.177 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
496 | 912.253 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
498 | 915.297 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
500 | 919.629 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928

## Pumping Costs
Option 8 Pumping Costs
PS 1
New Pipe - Year 4 to 18 |  | Average Pipe - Year 19 to 33 |  | Old Pipe - Year 34 to 48 |  | Biofilmed Pipe - Year 49 to 63
Pumping Head (m) | 50 | Pumping Head (m) | 50 | Pumping Head (m) | 50 | Pumping Head (m) | 50
Gravitational Head (m) | -32.652 | Gravitational Head (m) | -32.652 | Gravitational Head (m) | -32.652 | Gravitational Head (m) | -32.652
Flow Rate (m3/s) | 5.449 | Flow Rate (m3/s) | 5.1612 | Flow Rate (m3/s) | 4.7764 | Flow Rate (m3/s) | 4.2619
Pumping Hours per Day | 24 | Pumping Hours per Day | 24 | Pumping Hours per Day | 24 | Pumping Hours per Day | 24
Peak Design Flow (m3/s) | 4.083 | Peak Design Flow | 4.083 | Peak Design Flow | 4.083 | Peak Design Flow | 4.083
Required Pumping Hours | 18 | Required Pumping Hours | 19 | Required Pumping Hours | 20.5 | Required Pumping Hours | 23
Pumpstation Power (kW) | 2342 | Pumpstation Power (kW) | 2342 | Pumpstation Power (kW) | 2342 | Pumpstation Power (kW) | 2342
Pumping Days per Year | 347 | Pumping Days per Year | 347 | Pumping Days per Year | 347 | Pumping Days per Year | 347
Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699
Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388
Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056
Energy Cost Per Year | 6591195.5419 | Energy Cost Per Year | 6957353.9394 | Energy Cost Per Year | 7506591.5355 | Energy Cost Per Year | 8421987.5291
Option 8 Pumping Costs
PS 2
New Pipe - Year 4 to 18 |  | Average Pipe - Year 19 to 33 |  | Old Pipe - Year 34 to 48 |  | Biofilmed Pipe - Year 49 to 63
Pumping Head (m) | 160 | Pumping Head (m) | 160 | Pumping Head (m) | 160 | Pumping Head (m) | 160
Gravitational Head (m) | 188.186 | Gravitational Head (m) | 188.186 | Gravitational Head (m) | 188.186 | Gravitational Head (m) | 188.186
Flow Rate (m3/s) | 5.9553 | Flow Rate (m3/s) | 5.6374 | Flow Rate (m3/s) | 5.2127 | Flow Rate (m3/s) | 4.6451
Pumping Hours per Day | 24 | Pumping Hours per Day | 24 | Pumping Hours per Day | 24 | Pumping Hours per Day | 24
Peak Design Flow (m3/s) | 4.083 | Peak Design Flow | 4.083 | Peak Design Flow | 4.083 | Peak Design Flow | 4.083
Required Pumping Hours | 16.5 | Required Pumping Hours | 17.4 | Required Pumping Hours | 18.8 | Required Pumping Hours | 21.1
Pumpstation Power (kW) | 12177 | Pumpstation Power (kW) | 12177 | Pumpstation Power (kW) | 12177 | Pumpstation Power (kW) | 12177
Pumping Days per Year | 347 | Pumping Days per Year | 347 | Pumping Days per Year | 347 | Pumping Days per Year | 347
Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699
Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388
Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056
Energy Cost Per Year | 31413123.3346 | Energy Cost Per Year | 33126547.6407 | Energy Cost Per Year | 35791874.3392 | Energy Cost Per Year | 40170625.3439
Pipe Type | Energy Cost Per Year PS 1 | Energy Cost Per Year PS 2
New Pipe | 6591195.5419 | 31413123.3346
Average Pipe | 6957353.9394 | 33126547.6407
Old Pipe | 7506591.5355 | 35791874.3392
Biofilm Pipe | 8421987.5291 | 40170625.3439
Pipe Type | Energy Cost Per Year PS 1 (Pula) | Energy Cost Per Year PS 2 (Pula)
New Pipe | 5991995.9472 | 28557384.8496
Average Pipe | 6324867.2176 | 30115043.3098
Old Pipe | 6824174.1232 | 32538067.5811
Biofilm Pipe | 7656352.2992 | 36518750.3126

## Life Cycle Costing (Pula)
Table 43: Option 8 Life Cycle Costing (Pula)
Year | Reference Year | Capital Cost | Electricity - Pumping Cost | Maintenance Cost | NPV at 6% Discount Rate | NPV at 8% Discount Rate | NPV at 10% Discount Rate
2010 | 0 | 1841277449.4729 |  |  | 1841277449.4729 | 1841277449.4729 | 1841277449.4729
2011 | 1 | 1841277449.4729 |  |  | 1841277449.4729 | 1841277449.4729 | 1841277449.4729
2012 | 2 | 1841277449.4729 |  |  | 1841277449.4729 | 1841277449.4729 | 1841277449.4729
2013 | 3 | 1841277449.4729 |  |  | 1841277449.4729 | 1841277449.4729 | 1841277449.4729
2014 | 4 | 0 | 34549380.7968 | 43643568.5052 | 61936139.652 | 57474152.0152 | 53406836.488
2015 | 5 | 0 | 34549380.7968 | 43643568.5052 | 58430320.4264 | 53216807.4215 | 48551669.5345
2016 | 6 | 0 | 34549380.7968 | 43643568.5052 | 55122943.7985 | 49274821.6865 | 44137881.395
2017 | 7 | 0 | 34549380.7968 | 43643568.5052 | 52002777.1684 | 45624834.895 | 40125346.7227
2018 | 8 | 0 | 34549380.7968 | 43643568.5052 | 49059223.7438 | 42245217.4953 | 36477587.9298
2019 | 9 | 0 | 34549380.7968 | 43643568.5052 | 46282286.5508 | 39115942.1253 | 33161443.5725
2020 | 10 | 0 | 34549380.7968 | 43643568.5052 | 43662534.4818 | 36218464.9308 | 30146766.8841
2021 | 11 | 0 | 34549380.7968 | 43643568.5052 | 41191070.2659 | 33535615.6767 | 27406151.7128
2022 | 12 | 0 | 34549380.7968 | 43643568.5052 | 38859500.2508 | 31051495.9969 | 24914683.3753
2023 | 13 | 0 | 34549380.7968 | 43643568.5052 | 36659905.897 | 28751385.1824 | 22649712.1594
2024 | 14 | 0 | 34549380.7968 | 43643568.5052 | 34584816.884 | 26621652.9466 | 20590647.4176
2025 | 15 | 0 | 34549380.7968 | 43643568.5052 | 32627185.7396 | 24649678.6543 | 18718770.3796
2026 | 16 | 0 | 34549380.7968 | 43643568.5052 | 30780363.9053 | 22823776.5317 | 17017063.9815
2027 | 17 | 0 | 34549380.7968 | 43643568.5052 | 29038079.1559 | 21133126.4183 | 15470058.165
2028 | 18 | 0 | 34549380.7968 | 43643568.5052 | 27394414.298 | 19567709.6466 | 14063689.2409
2029 | 19 | 0 | 36439910.5274 | 43643568.5052 | 26468631.7463 | 18556308.2187 | 13094288.755
2030 | 20 | 0 | 36439910.5274 | 43643568.5052 | 24970407.3078 | 17181766.8691 | 11903898.8682
2031 | 21 | 0 | 36439910.5274 | 43643568.5052 | 23556988.0263 | 15909043.3973 | 10821726.2438
2032 | 22 | 0 | 36439910.5274 | 43643568.5052 | 22223573.6097 | 14730595.7383 | 9837932.9489
2033 | 23 | 0 | 36439910.5274 | 43643568.5052 | 20965635.4808 | 13639440.4984 | 8943575.4081
2034 | 24 | 0 | 36439910.5274 | 43643568.5052 | 19778901.397 | 12629111.5726 | 8130523.0983
2035 | 25 | 0 | 36439910.5274 | 43643568.5052 | 18659340.9406 | 11693621.8265 | 7391384.6348
2036 | 26 | 0 | 36439910.5274 | 43643568.5052 | 17603151.8307 | 10827427.6171 | 6719440.5771
2037 | 27 | 0 | 36439910.5274 | 43643568.5052 | 16606747.0101 | 10025395.9418 | 6108582.3428
2038 | 28 | 0 | 36439910.5274 | 43643568.5052 | 15666742.4624 | 9282774.0202 | 5553256.6753
2039 | 29 | 0 | 36439910.5274 | 43643568.5052 | 14779945.7192 | 8595161.1298 | 5048415.1594
2040 | 30 | 0 | 36439910.5274 | 43643568.5052 | 13943345.0181 | 7958482.5276 | 4589468.3267
2041 | 31 | 0 | 36439910.5274 | 43643568.5052 | 13154099.0737 | 7368965.3033 | 4172243.9333
2042 | 32 | 0 | 36439910.5274 | 43643568.5052 | 12409527.428 | 6823116.0216 | 3792949.0303
2043 | 33 | 0 | 36439910.5274 | 43643568.5052 | 11707101.3472 | 6317700.02 | 3448135.4821
2044 | 34 | 0 | 39362241.7043 | 43643568.5052 | 11447458.4011 | 6063184.8161 | 3249056.0062
2045 | 35 | 0 | 39362241.7043 | 43643568.5052 | 10799489.0576 | 5614060.0149 | 2953687.2784
2046 | 36 | 0 | 39362241.7043 | 43643568.5052 | 10188197.2242 | 5198203.7175 | 2685170.2531
2047 | 37 | 0 | 39362241.7043 | 43643568.5052 | 9611506.8153 | 4813151.5903 | 2441063.8664
2048 | 38 | 0 | 39362241.7043 | 43643568.5052 | 9067459.2597 | 4456621.8429 | 2219148.9695
2049 | 39 | 0 | 39362241.7043 | 43643568.5052 | 8554206.8488 | 4126501.7064 | 2017408.1541
2050 | 40 | 0 | 39362241.7043 | 43643568.5052 | 8070006.4611 | 3820834.9133 | 1834007.4128
2051 | 41 | 0 | 39362241.7043 | 43643568.5052 | 7613213.6425 | 3537810.1049 | 1667279.4662
2052 | 42 | 0 | 39362241.7043 | 43643568.5052 | 7182277.0213 | 3275750.0971 | 1515708.6056
2053 | 43 | 0 | 39362241.7043 | 43643568.5052 | 6775733.0389 | 3033101.9418 | 1377916.9142
2054 | 44 | 0 | 39362241.7043 | 43643568.5052 | 6392200.9801 | 2808427.7239 | 1252651.7402
2055 | 45 | 0 | 39362241.7043 | 43643568.5052 | 6030378.2831 | 2600396.0406 | 1138774.3093
2056 | 46 | 0 | 39362241.7043 | 43643568.5052 | 5689036.1162 | 2407774.1117 | 1035249.372
2057 | 47 | 0 | 39362241.7043 | 43643568.5052 | 5367015.2039 | 2229420.4738 | 941135.7928
2058 | 48 | 0 | 39362241.7043 | 43643568.5052 | 5063221.8905 | 2064278.2165 | 855577.9934
2059 | 49 | 0 | 44175102.6118 | 43643568.5052 | 5053583.6994 | 2022194.115 | 822896.6385
2060 | 50 | 0 | 44175102.6118 | 43643568.5052 | 4767531.7919 | 1872401.9583 | 748087.8532
2061 | 51 | 0 | 44175102.6118 | 43643568.5052 | 4497671.5018 | 1733705.5169 | 680079.8666
2062 | 52 | 0 | 44175102.6118 | 43643568.5052 | 4243086.3224 | 1605282.8861 | 618254.4241
2063 | 53 | 0 | 44175102.6118 | 43643568.5052 | 4002911.6249 | 1486373.0426 | 562049.4765
2064 | 54 | 0 | 44175102.6118 | 43643568.5052 | 3776331.7216 | 1376271.3358 | 510954.0695
2065 | 55 | 0 | 44175102.6118 | 43643568.5052 | 3562577.0959 | 1274325.3109 | 464503.6996
2066 | 56 | 0 | 44175102.6118 | 43643568.5052 | 3360921.7886 | 1179930.8434 | 422276.0905
2067 | 57 | 0 | 44175102.6118 | 43643568.5052 | 3170680.9326 | 1092528.5587 | 383887.355
2068 | 58 | 0 | 44175102.6118 | 43643568.5052 | 2991208.427 | 1011600.5173 | 348988.5046
2069 | 59 | 0 | 44175102.6118 | 43643568.5052 | 2821894.7424 | 936667.1457 | 317262.2769
2070 | 60 | 0 | 44175102.6118 | 43643568.5052 | 2662164.8514 | 867284.3942 | 288420.2517
2071 | 61 | 0 | 44175102.6118 | 43643568.5052 | 2511476.2749 | 803041.1057 | 262200.2288
2072 | 62 | 0 | 44175102.6118 | 43643568.5052 | 2369317.2404 | 743556.5794 | 238363.8444
2073 | 63 | 0 | 44175102.6118 | 43643568.5052 | 2235204.9438 | 688478.3142 | 216694.404
[5 empty] | 8445113461.7112 | 8142696549.1526 | 7955572683.4524

## Life Cycle Costing
Table 43: Option 8 Life Cycle Costing
Year | Reference Year | Capital Cost | Electricity - Pumping Cost | Maintenance Cost | NPV at 6% Discount Rate | NPV at 8% Discount Rate | NPV at 10% Discount Rate
2010 | 0 | 2025405194.4202 |  |  | 2025405194.4202 | 2025405194.4202 | 2025405194.4202
2011 | 1 | 2025405194.4202 |  |  | 2025405194.4202 | 2025405194.4202 | 2025405194.4202
2012 | 2 | 2025405194.4202 |  |  | 2025405194.4202 | 2025405194.4202 | 2025405194.4202
2013 | 3 | 2025405194.4202 |  |  | 2025405194.4202 | 2025405194.4202 | 2025405194.4202
2014 | 4 | 0 | 38004318.8765 | 48007925.3558 | 68129753.6172 | 63221567.2167 | 58747520.1368
2015 | 5 | 0 | 38004318.8765 | 48007925.3558 | 64273352.4691 | 58538488.1636 | 53406836.488
2016 | 6 | 0 | 38004318.8765 | 48007925.3558 | 60635238.1784 | 54202303.8552 | 48551669.5345
2017 | 7 | 0 | 38004318.8765 | 48007925.3558 | 57203054.8853 | 50187318.3844 | 44137881.395
2018 | 8 | 0 | 38004318.8765 | 48007925.3558 | 53965146.1182 | 46469739.2449 | 40125346.7227
2019 | 9 | 0 | 38004318.8765 | 48007925.3558 | 50910515.2058 | 43027536.3378 | 36477587.9298
2020 | 10 | 0 | 38004318.8765 | 48007925.3558 | 48028787.93 | 39840311.4239 | 33161443.5725
2021 | 11 | 0 | 38004318.8765 | 48007925.3558 | 45310177.2925 | 36889177.2444 | 30146766.8841
2022 | 12 | 0 | 38004318.8765 | 48007925.3558 | 42745450.2759 | 34156645.5966 | 27406151.7128
2023 | 13 | 0 | 38004318.8765 | 48007925.3558 | 40325896.4867 | 31626523.7006 | 24914683.3753
2024 | 14 | 0 | 38004318.8765 | 48007925.3558 | 38043298.5724 | 29283818.2413 | 22649712.1594
2025 | 15 | 0 | 38004318.8765 | 48007925.3558 | 35889904.3136 | 27114646.5197 | 20590647.4176
2026 | 16 | 0 | 38004318.8765 | 48007925.3558 | 33858400.2958 | 25106154.1849 | 18718770.3796
2027 | 17 | 0 | 38004318.8765 | 48007925.3558 | 31941887.0715 | 23246439.0601 | 17017063.9815
2028 | 18 | 0 | 38004318.8765 | 48007925.3558 | 30133855.7279 | 21524480.6112 | 15470058.165
2029 | 19 | 0 | 40083901.5801 | 48007925.3558 | 29115494.9209 | 20411939.0405 | 14403717.6305
2030 | 20 | 0 | 40083901.5801 | 48007925.3558 | 27467448.0386 | 18899943.556 | 13094288.755
2031 | 21 | 0 | 40083901.5801 | 48007925.3558 | 25912686.8289 | 17499947.7371 | 11903898.8682
2032 | 22 | 0 | 40083901.5801 | 48007925.3558 | 24445930.9707 | 16203655.3121 | 10821726.2438
2033 | 23 | 0 | 40083901.5801 | 48007925.3558 | 23062199.0289 | 15003384.5482 | 9837932.9489
2034 | 24 | 0 | 40083901.5801 | 48007925.3558 | 21756791.5367 | 13892022.7299 | 8943575.4081
2035 | 25 | 0 | 40083901.5801 | 48007925.3558 | 20525275.0346 | 12862984.0091 | 8130523.0983
2036 | 26 | 0 | 40083901.5801 | 48007925.3558 | 19363467.0138 | 11910170.3788 | 7391384.6348
2037 | 27 | 0 | 40083901.5801 | 48007925.3558 | 18267421.7111 | 11027935.5359 | 6719440.5771
2038 | 28 | 0 | 40083901.5801 | 48007925.3558 | 17233416.7086 | 10211051.4222 | 6108582.3428
2039 | 29 | 0 | 40083901.5801 | 48007925.3558 | 16257940.2912 | 9454677.2427 | 5553256.6753
2040 | 30 | 0 | 40083901.5801 | 48007925.3558 | 15337679.52 | 8754330.7803 | 5048415.1594
2041 | 31 | 0 | 40083901.5801 | 48007925.3558 | 14469508.9811 | 8105861.8336 | 4589468.3267
2042 | 32 | 0 | 40083901.5801 | 48007925.3558 | 13650480.1708 | 7505427.6237 | 4172243.9333
2043 | 33 | 0 | 40083901.5801 | 48007925.3558 | 12877811.4819 | 6949470.022 | 3792949.0303
2044 | 34 | 0 | 43298465.8748 | 48007925.3558 | 12592204.2412 | 6669503.2977 | 3573961.6068
2045 | 35 | 0 | 43298465.8748 | 48007925.3558 | 11879437.9634 | 6175466.0164 | 3249056.0062
2046 | 36 | 0 | 43298465.8748 | 48007925.3558 | 11207016.9466 | 5718024.0893 | 2953687.2784
2047 | 37 | 0 | 43298465.8748 | 48007925.3558 | 10572657.4968 | 5294466.7493 | 2685170.2531
2048 | 38 | 0 | 43298465.8748 | 48007925.3558 | 9974205.1856 | 4902284.0272 | 2441063.8664
2049 | 39 | 0 | 43298465.8748 | 48007925.3558 | 9409627.5336 | 4539151.877 | 2219148.9695
2050 | 40 | 0 | 43298465.8748 | 48007925.3558 | 8877007.1072 | 4202918.4046 | 2017408.1541
2051 | 41 | 0 | 43298465.8748 | 48007925.3558 | 8374535.0068 | 3891591.1154 | 1834007.4128
2052 | 42 | 0 | 43298465.8748 | 48007925.3558 | 7900504.7234 | 3603325.1068 | 1667279.4662
2053 | 43 | 0 | 43298465.8748 | 48007925.3558 | 7453306.3428 | 3336412.136 | 1515708.6056
2054 | 44 | 0 | 43298465.8748 | 48007925.3558 | 7031421.0781 | 3089270.4963 | 1377916.9142
2055 | 45 | 0 | 43298465.8748 | 48007925.3558 | 6633416.1114 | 2860435.6447 | 1252651.7402
2056 | 46 | 0 | 43298465.8748 | 48007925.3558 | 6257939.7278 | 2648551.5229 | 1138774.3093
2057 | 47 | 0 | 43298465.8748 | 48007925.3558 | 5903716.7243 | 2452362.5212 | 1035249.372
2058 | 48 | 0 | 43298465.8748 | 48007925.3558 | 5569544.0795 | 2270706.0381 | 941135.7928
2059 | 49 | 0 | 48592612.873 | 48007925.3558 | 5558942.0693 | 2224413.5265 | 905186.3024
2060 | 50 | 0 | 48592612.873 | 48007925.3558 | 5244284.9711 | 2059642.1541 | 822896.6385
2061 | 51 | 0 | 48592612.873 | 48007925.3558 | 4947438.6519 | 1907076.0686 | 748087.8532
2062 | 52 | 0 | 48592612.873 | 48007925.3558 | 4667394.9547 | 1765811.1747 | 680079.8666
2063 | 53 | 0 | 48592612.873 | 48007925.3558 | 4403202.7874 | 1635010.3469 | 618254.4241
2064 | 54 | 0 | 48592612.873 | 48007925.3558 | 4153964.8938 | 1513898.4694 | 562049.4765
2065 | 55 | 0 | 48592612.873 | 48007925.3558 | 3918834.8055 | 1401757.842 | 510954.0695
2066 | 56 | 0 | 48592612.873 | 48007925.3558 | 3697013.9674 | 1297923.9278 | 464503.6996
2067 | 57 | 0 | 48592612.873 | 48007925.3558 | 3487749.0259 | 1201781.4146 | 422276.0905
2068 | 58 | 0 | 48592612.873 | 48007925.3558 | 3290329.2697 | 1112760.5691 | 383887.355
2069 | 59 | 0 | 48592612.873 | 48007925.3558 | 3104084.2167 | 1030333.8603 | 348988.5046
2070 | 60 | 0 | 48592612.873 | 48007925.3558 | 2928381.3365 | 954012.8336 | 317262.2769
2071 | 61 | 0 | 48592612.873 | 48007925.3558 | 2762623.9023 | 883345.2163 | 288420.2517
2072 | 62 | 0 | 48592612.873 | 48007925.3558 | 2606248.9645 | 817912.2373 | 262200.2288
2073 | 63 | 0 | 48592612.873 | 48007925.3558 | 2458725.4382 | 757326.1456 | 238363.8444
[5 empty] | 9289624807.8823 | 8956966204.0679 | 8751129951.7977