## Summary
Option 5B Summary
Item | Chainage | Value
Pipeline | 0-8 | 1.9 | m - Diameter
Pump Station | 8 | 50 | m - Pumping Head
Pipeline | 8-22 | 1.9 | m - Diameter
Break Pressure | 22 | 10 | m -Elevation
Pipeline | 22-164 | 1.9 | m - Diameter
Pipeline | 164-226 | 1.8 | m - Diameter
Pipeline | 226-228 | 2 | m - Diameter
Break Pressure | 228 | 10 | m - Elevation
Pump Station | 228 | 120 | m - Pumping Head
Pipeline | 228-274 | 2 | m -Diameter
Pipeline | 274-330 | 2 | m -Diameter
Break Pressure | 330 | 10 | m - Elevation
Pipeline | 330-482 | 1.8 | m -Diameter
Pipeline | 482-500 | 1.5 | m -Diameter
B

## Profile data
Longitudinal profile data - Botswana pipeline
| OPTION 1: Pipeline goes through Serule before joining to BPT1 | OPTION2: Pipeline goes directly to BPT1
CHAINAGE (km0 | NGL (m) | NGL (m) |  | Botswana 1
2 | 1069.018 | 1069.018 | Start | Botswana 2
4 | 1067.321 | 1067.321
6 | 1064.035 | 1064.035
8 | 1063.832 | 1063.832
10 | 1067.893 | 1067.893
12 | 1075.133 | 1075.133
14 | 1082.768 | 1082.768
16 | 1089.726 | 1089.726
18 | 1094.131 | 1094.131
20 | 1097.897 | 1097.897
22 | 1101.67 | 1101.67
24 | 1095.952 | 1095.952
26 | 1090.107 | 1090.107
28 | 1085.781 | 1085.781
30 | 1081.89 | 1081.89
32 | 1077.937 | 1077.937
34 | 1074.89 | 1074.89
36 | 1071.114 | 1071.114
38 | 1065.311 | 1065.311
40 | 1059.051 | 1059.051
42 | 1054.28 | 1054.28
44 | 1053.871 | 1053.871
46 | 1050.42 | 1050.42
48 | 1052.704 | 1052.704
50 | 1056.355 | 1056.355
52 | 1058.466 | 1058.466
54 | 1055.99 | 1055.99
56 | 1055.66 | 1055.66
58 | 1056.404 | 1056.404
60 | 1056.841 | 1056.841
62 | 1056.377 | 1056.377
64 | 1052.503 | 1052.503
66 | 1046.022 | 1046.022
68 | 1036.575 | 1036.575
70 | 1031.818 | 1031.818
72 | 1027.675 | 1027.675
74 | 1023.844 | 1023.844
76 | 1020.888 | 1020.888
78 | 1023.648 | 1023.648
80 | 1027.566 | 1027.566
82 | 1032.371 | 1032.371
84 | 1034.983 | 1034.983
86 | 1033.213 | 1033.213
88 | 1031.188 | 1031.188
90 | 1029.08 | 1029.08
92 | 1026.322 | 1026.322
94 | 1023.207 | 1023.207
96 | 1021.503 | 1021.503
98 | 1019.765 | 1019.765
100 | 1018.493 | 1018.493
102 | 1016.444 | 1016.444
104 | 1013.288 | 1013.288
106 | 1007.843 | 1007.843
108 | 1001.282 | 1001.282
110 | 996.609 | 996.609
112 | 992.999 | 992.999
114 | 993.639 | 993.639
116 | 994.611 | 994.611
118 | 995.751 | 995.751
120 | 996.479 | 996.479
122 | 996.147 | 996.147
124 | 992.094 | 992.094
126 | 985.623 | 985.623
128 | 977.759 | 977.759
130 | 969.772 | 969.772
132 | 981.785 | 981.785
134 | 991.458 | 991.458
136 | 987.77 | 987.77
138 | 982.725 | 982.725
140 | 977.559 | 977.559
142 | 975.289 | 975.289
144 | 973.968 | 973.968
146 | 962.473 | 962.473
148 | 951.285 | 951.285
150 | 948.174 | 948.174
152 | 944.641 | 944.641
154 | 941.566 | 941.566
156 | 940.942 | 940.942
158 | 939.726 | 939.726
160 | 936.738 | 936.738
162 | 933.65 | 933.65
164 | 932.745 | 932.745
166 | 931.696 | 931.696
168 | 930.999 | 930.999
170 | 930.885 | 930.885
172 | 930.378 | 930.378
174 | 931.324 | 931.324
176 | 933.53 | 933.53
178 | 932.714 | 932.714
180 | 928.311 | 928.311
182 | 924.179 | 924.179
184 | 928.398 | 928.398
186 | 930.866 | 930.866
188 | 928.411 | 928.411
190 | 927.849 | 927.849
192 | 926.71 | 926.71
194 | 926.201 | 926.201
196 | 924.509 | 924.509
198 | 923.417 | 923.417
200 | 923.011 | 923.011
202 | 921.969 | 921.969
204 | 920.661 | 920.661
206 | 920.243 | 920.243
208 | 919.297 | 919.297
210 | 917.533 | 917.533
212 | 917.684 | 917.684
214 | 915.724 | 915.724
216 | 915.73 | 915.73
218 | 915.584 | 915.584
220 | 915.444 | 915.444
222 | 913.52 | 913.52
224 | 912.524 | 912.524
226 | 912.565 | 912.565
228 | 913.484 | 913.484
230 | 913.545 | 913.545
232 | 914.546 | 914.546
234 | 918.285 | 918.285
236 | 919.357 | 919.357
238 | 918.649 | 918.649
240 | 922.974 | 922.974
242 | 927.375 | 927.375
244 | 929.253 | 929.253
246 | 930.863 | 930.863
248 | 931.924 | 931.924
250 | 936.722 | 936.722
252 | 941.777 | 941.777
254 | 948.143 | 948.143
256 | 955.417 | 955.417
258 | 962.7 | 962.7
260 | 969.281 | 969.281
262 | 980.284 | 980.284
264 | 986.551 | 986.551
266 | 989.198 | 989.198
268 | 994.39 | 994.39
270 | 999.917 | 999.917
272 | 1004.623 | 1004.623
274 | 1008.819 | 1008.819
276 | 1007.834 | 1007.834
278 | 1005.626 | 1005.626
280 | 1001.623 | 1001.623
282 | 1004.052 | 1004.052
284 | 1010.797 | 1010.797
286 | 1014.67 | 1014.67
288 | 1017.319 | 1017.319
290 | 1027.459 | 1027.459
292 | 1031.99 | 1031.99
294 | 1036.254 | 1036.254
296 | 1040.127 | 1040.127
298 | 1044.396 | 1044.396
300 | 1051.339 | 1051.339
302 | 1060.955 | 1060.955
304 | 1070.227 | 1070.227
306 | 1072.691 | 1072.691
308 | 1076.503 | 1076.503
310 | 1083.996 | 1083.996
312 | 1097.188 | 1097.188
314 | 1103.545 | 1103.545
316 | 1105.174 | 1105.174
318 | 1111.657 | 1111.657
320 | 1122.935 | 1122.935
322 | 1128.197 | 1128.197
324 | 1132.561 | 1132.561
326 | 1131.854 | 1131.854
328 | 1133.338 | 1133.338
330 | 1136.405 | 1136.405
332 | 1128.709 | 1128.709
334 | 1120.713 | 1120.713
336 | 1115.226 | 1115.226
338 | 1108.709 | 1108.709
340 | 1102.499 | 1102.499
342 | 1096.349 | 1096.349
344 | 1090.39 | 1090.39
346 | 1087.765 | 1087.765
348 | 1084.661 | 1084.661
350 | 1081.662 | 1081.662
352 | 1076.872 | 1076.872
354 | 1070.898 | 1070.898
356 | 1065.018 | 1065.018
358 | 1059.58 | 1059.58
360 | 1055.284 | 1055.284
362 | 1050.886 | 1050.886
364 | 1052.647 | 1052.647
366 | 1051.117 | 1051.117
368 | 1048.266 | 1048.266
370 | 1040.172 | 1040.172
372 | 1033.483 | 1033.483
374 | 1030.95 | 1030.95
376 | 1032.263 | 1032.263
378 | 1031.391 | 1031.391
380 | 1025.791 | 1025.791
382 | 1020.911 | 1020.911
384 | 1015.65 | 1015.65
386 | 1012.139 | 1012.139
388 | 1010.472 | 1010.472
390 | 1005.401 | 1005.401
392 | 996.666 | 996.666
394 | 991.35 | 991.35
396 | 990.486 | 990.486
398 | 992.761 | 992.761
400 | 999.077 | 999.077
402 | 1001.8 | 1001.8
404 | 1002.224 | 1002.224
406 | 1002.003 | 1002.003
408 | 1003.596 | 1003.596
410 | 994.111 | 994.111
412 | 983.925 | 983.925
414 | 972.347 | 972.347
416 | 963.901 | 963.901
418 | 963.258 | 963.258
420 | 965.836 | 965.872
422 | 966.309 | 966.177
424 | 972.884 | 973.825
426 | 983.972 | 983.972
428 | 994.096 | 994.096
430 | 991.695 | 991.695
432 | 984.933 | 984.933
434 | 978.185 | 974.509
436 | 972.686 | 966.698
438 | 966.824 | 963.618
440 | 960.902 | 957.803
442 | 952.924 | 954.277
444 | 945.683 | 947.182
446 | 941.042 | 938.045
448 | 937.104 | 930.871
450 | 939.943 | 926.391
452 | 944.776 | 918.344
454 | 947.762 | 911.505
456 | 952.649 | 903.61
458 | 954.554 | 900.63
460 | 952.37 | 904.066
462 | 947.552 | 915.092
464 | 941.898 | 905.556
466 | 940.521 | 905.271
468 | 939.702 | 901.918
470 | 937.147 | 895.651
472 | 933.872 | 892.304
474 | 933.184 | 895.279
476 | 939.292 | 896.818
478 | 944.619 | 909.921
480 | 954.023 | 926.295
482 | 968.263 | 924.888
484 | 970.384 | 919.044
486 | 964.636 | 911.164
488 | 956.631 | 903.893
490 | 947.426 | 901.953
492 | 941.72 | 900.198
494 | 935.985 | 904.177
496 | 930.475 | 912.253
498 | 927.611 | 915.297
500 | 931.256 | 919.629
502 | 920.044
504 | 911.78
506 | 907.989
508 | 907.289
510 | 900.577
512 | 902.112
514 | 900.179
516 | 903.811
518 | 910.027
520 | 911.131 |  | End

## Flow Rate Calculations
Estimated Transfer Rate Demand | 100 | Mm3/a
Availible Days | 365
Pumping Hours | 24
Pf | 1.052
Pl | 1.02
PR | 1.2
Peak Design Flow | 4.0831 | m3/s

## Calculation Constants
Friction Factors
Ks (mm) - New | 0.03
Ks (mm) - Average | 0.06
Ks (mm) - Old | 0.15
Ks (mm) - Biofilm | 0.5
Kinemeatic Viscosity | 1.13e-06 | m2/s
Minor Loss - k | 150
Grade of Steel | X42
Yeild Capacity | 300 | Mpa
Design % of Yeild | 50%
Minimum D/t ratio | 160 | mm/mm

## Hydraulics
Option 5B |  |  |  | Option 5B | [12 empty] | Option 5B
Pump Station |  |  |  | Pipe Line | [9 empty] | Steel Pipeline Design |  |  | New Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Average Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Old Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Biofilm Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes
Name | Chainage (km) | Elevation (m) | Pumped Head (m) | Reference | Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Flow Rate (m3/s) | PipeVelocity (m/s) | Re | Static Head (m) | Dynamic Head (m) | Design Pressure (m) | Pipe Wall thickness (mm) | Steel Mass (kg) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m)
PS 1 | 8 | 1063.832 | 50 | Reservoir | 2 | 1069.018 | 0 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 10 | 10 | 10 | 11.875 | 0 | 0.00867 |  |  | 0 | 0 | 10 | 1079.018 | 0.0097304 |  |  | 0 | 0 | 10 | 1079.018 | 0.011459 |  |  | 0 | 0 | 10 | 1079.018 | 0.014543 |  |  | 0 | 0 | 10 | 1079.018
PS 3 | 228 | 913.484 | 120 |  | 4 | 1067.321 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 11.697 | 10.6689 | 11.697 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 10.6689 | 1077.9899 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 10.5509 | 1077.8719 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 10.3586 | 1077.6796 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 10.0086 | 1077.3296
[5 empty] | 6 | 1064.035 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 14.983 | 12.9268 | 14.983 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 12.9268 | 1076.9618 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 12.6908 | 1076.7258 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 12.3062 | 1076.3412 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 11.6062 | 1075.6412
|  |  |  | Pump Station | 8 | 1063.832 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 62.1017 | 61.7477 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 50 | 62.1017 | 1125.9337 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 50 | 61.7477 | 1125.5797 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 50 | 61.1707 | 1125.0027 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 50 | 60.1208 | 1123.9528
[5 empty] | 10 | 1067.893 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 57.0126 | 56.5407 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 57.0126 | 1124.9056 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 56.5407 | 1124.4337 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 55.7713 | 1123.6643 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 54.3714 | 1122.2644
Reservoirs |  |  |  |  | 12 | 1075.133 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 48.7445 | 48.1546 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 48.7445 | 1123.8775 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 48.1546 | 1123.2876 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 47.1929 | 1122.3259 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 45.443 | 1120.576
Name | Chainage (km) | Water Elevation (m) | Height |  | 14 | 1082.768 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 40.0814 | 39.3735 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 40.0814 | 1122.8494 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 39.3735 | 1122.1415 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 38.2195 | 1120.9875 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 36.1196 | 1118.8876
Supply Resrvoir | 2 | 1079.018 | 10 |  | 16 | 1089.726 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 32.0953 | 31.2694 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 32.0953 | 1121.8213 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 31.2694 | 1120.9954 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 29.9231 | 1119.6491 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.4732 | 1117.1992
BPT 3 | 22 | 1111.67 | 10 |  | 18 | 1094.131 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 26.6622 | 25.7183 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 26.6622 | 1120.7932 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 25.7183 | 1119.8493 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 24.1796 | 1118.3106 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 21.3798 | 1115.5108
BPT 5 | 228 | 923.484 | 10 |  | 20 | 1097.897 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 21.8681 | 20.8062 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 21.8681 | 1119.7651 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 20.8062 | 1118.7032 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 19.0752 | 1116.9722 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 15.9254 | 1113.8224
|  |  |  | Reservoir | 22 | 1101.67 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 10 | 10 | 10 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 10 | 1111.67 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 10 | 1111.67 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 10 | 1111.67 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 10 | 1111.67
BPT 2 | 330 | 1146.405 | 10 |  | 24 | 1095.952 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 15.718 | 14.6899 | 15.718 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 14.6899 | 1110.6419 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 14.5719 | 1110.5239 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 14.3796 | 1110.3316 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 14.0296 | 1109.9816
BPT 1 | 500 | 929.629 | 10 |  | 26 | 1090.107 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 21.563 | 19.5068 | 21.563 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 19.5068 | 1109.6138 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 19.2708 | 1109.3778 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 18.8862 | 1108.9932 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 18.1862 | 1108.2932
[5 empty] | 28 | 1085.781 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 25.889 | 22.8047 | 25.889 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 22.8047 | 1108.5857 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 22.4507 | 1108.2317 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 21.8737 | 1107.6547 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 20.8238 | 1106.6048
|  | -1146.405 |  |  | 30 | 1081.89 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 29.78 | 25.6676 | 29.78 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 25.6676 | 1107.5576 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 25.1957 | 1107.0857 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 24.4263 | 1106.3163 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 23.0264 | 1104.9164
[5 empty] | 32 | 1077.937 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 33.733 | 28.5925 | 33.733 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 28.5925 | 1106.5295 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 28.0026 | 1105.9396 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 27.0409 | 1104.9779 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 25.291 | 1103.228
[5 empty] | 34 | 1074.89 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 36.78 | 30.6114 | 36.78 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 30.6114 | 1105.5014 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 29.9035 | 1104.7935 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 28.7495 | 1103.6395 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 26.6496 | 1101.5396
[5 empty] | 36 | 1071.114 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 40.556 | 33.3593 | 40.556 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 33.3593 | 1104.4733 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 32.5334 | 1103.6474 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 31.1871 | 1102.3011 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 28.7372 | 1099.8512
Route | Botswana 2 |  |  |  | 38 | 1065.311 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 46.359 | 38.1342 | 46.359 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 38.1342 | 1103.4452 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 37.1903 | 1102.5013 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 35.6516 | 1100.9626 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 32.8518 | 1098.1628
Option | 5B |  |  |  | 40 | 1059.051 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 52.619 | 43.3661 | 52.619 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 43.3661 | 1102.4171 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 42.3042 | 1101.3552 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 40.5732 | 1099.6242 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 37.4234 | 1096.4744
[5 empty] | 42 | 1054.28 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 57.39 | 47.109 | 57.39 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 47.109 | 1101.389 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 45.9292 | 1100.2092 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 44.0058 | 1098.2858 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 40.506 | 1094.786
[5 empty] | 44 | 1053.871 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 57.799 | 46.4899 | 57.799 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 46.4899 | 1100.3609 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 45.1921 | 1099.0631 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 43.0764 | 1096.9474 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 39.2267 | 1093.0977
[5 empty] | 46 | 1050.42 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 61.25 | 48.9128 | 61.25 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 48.9128 | 1099.3328 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 47.497 | 1097.917 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 45.1889 | 1095.6089 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 40.9893 | 1091.4093
[5 empty] | 48 | 1052.704 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 58.966 | 45.6007 | 58.966 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 45.6007 | 1098.3047 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 44.0669 | 1096.7709 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 41.5665 | 1094.2705 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 37.0169 | 1089.7209
[5 empty] | 50 | 1056.355 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.315 | 40.9216 | 55.315 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 40.9216 | 1097.2766 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 39.2698 | 1095.6248 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 36.5771 | 1092.9321 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 31.6775 | 1088.0325
[5 empty] | 52 | 1058.466 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 53.204 | 37.7825 | 53.204 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 37.7825 | 1096.2485 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 36.0127 | 1094.4787 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 33.1277 | 1091.5937 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.8781 | 1086.3441
[5 empty] | 54 | 1055.99 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.68 | 39.2304 | 55.68 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 39.2304 | 1095.2204 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 37.3426 | 1093.3326 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 34.2653 | 1090.2553 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 28.6657 | 1084.6557
[5 empty] | 56 | 1055.66 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 56.01 | 38.5323 | 56.01 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 38.5323 | 1094.1923 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 36.5266 | 1092.1866 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 33.2568 | 1088.9168 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.3073 | 1082.9673
[5 empty] | 58 | 1056.404 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.266 | 36.7602 | 55.266 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 36.7602 | 1093.1642 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 34.6365 | 1091.0405 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 31.1744 | 1087.5784 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 24.8749 | 1081.2789
[5 empty] | 60 | 1056.841 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 54.829 | 35.2951 | 54.829 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 35.2951 | 1092.1361 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 33.0534 | 1089.8944 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 29.399 | 1086.24 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 22.7495 | 1079.5905
[5 empty] | 62 | 1056.377 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.293 | 34.731 | 55.293 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 34.731 | 1091.108 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 32.3713 | 1088.7483 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 28.5246 | 1084.9016 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 21.5251 | 1077.9021
[5 empty] | 64 | 1052.503 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 59.167 | 37.5769 | 59.167 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 37.5769 | 1090.0799 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 35.0992 | 1087.6022 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 31.0602 | 1083.5632 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 23.7107 | 1076.2137
[5 empty] | 66 | 1046.022 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 65.648 | 43.0298 | 65.648 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 43.0298 | 1089.0518 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 40.4341 | 1086.4561 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 36.2027 | 1082.2247 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 28.5033 | 1074.5253
[5 empty] | 68 | 1036.575 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 75.095 | 51.4487 | 75.095 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 51.4487 | 1088.0237 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 48.735 | 1085.31 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 44.3113 | 1080.8863 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 36.2619 | 1072.8369
[5 empty] | 70 | 1031.818 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 79.852 | 55.1776 | 79.852 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 55.1776 | 1086.9956 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 52.346 | 1084.164 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 47.7299 | 1079.5479 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 39.3305 | 1071.1485
[5 empty] | 72 | 1027.675 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 83.995 | 58.2925 | 83.995 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 58.2925 | 1085.9675 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 55.3429 | 1083.0179 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 50.5345 | 1078.2095 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 41.7851 | 1069.4601
[5 empty] | 74 | 1023.844 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 87.826 | 61.0954 | 87.826 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 61.0954 | 1084.9394 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 58.0278 | 1081.8718 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 53.0271 | 1076.8711 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 43.9277 | 1067.7717
[5 empty] | 76 | 1020.888 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 90.782 | 63.0233 | 90.782 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 63.0233 | 1083.9113 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 59.8377 | 1080.7257 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 54.6446 | 1075.5326 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 45.1953 | 1066.0833
[5 empty] | 78 | 1023.648 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 88.022 | 59.2352 | 88.022 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 59.2352 | 1082.8832 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 55.9316 | 1079.5796 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 50.5462 | 1074.1942 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 40.7469 | 1064.3949
[5 empty] | 80 | 1027.566 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 84.104 | 54.2891 | 84.104 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 54.2891 | 1081.8551 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 50.8675 | 1078.4335 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 45.2898 | 1072.8558 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 35.1405 | 1062.7065
[5 empty] | 82 | 1032.371 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 79.299 | 48.456 | 79.299 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 48.456 | 1080.827 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 44.9165 | 1077.2875 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 39.1464 | 1071.5174 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 28.6471 | 1061.0181
[5 empty] | 84 | 1034.983 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 76.687 | 44.8159 | 76.687 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 44.8159 | 1079.7989 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 41.1584 | 1076.1414 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 35.1959 | 1070.1789 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 24.3468 | 1059.3298
[5 empty] | 86 | 1033.213 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 78.457 | 45.5578 | 78.457 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 45.5578 | 1078.7708 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 41.7823 | 1074.9953 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 35.6275 | 1068.8405 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 24.4284 | 1057.6414
[5 empty] | 88 | 1031.188 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 80.482 | 46.5547 | 80.482 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 46.5547 | 1077.7427 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 42.6612 | 1073.8492 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 36.3141 | 1067.5021 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 24.765 | 1055.953
[5 empty] | 90 | 1029.08 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 82.59 | 47.6346 | 82.59 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 47.6346 | 1076.7146 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 43.6231 | 1072.7031 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 37.0837 | 1066.1637 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 25.1846 | 1054.2646
[5 empty] | 92 | 1026.322 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 85.348 | 49.3645 | 85.348 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 49.3645 | 1075.6865 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 45.235 | 1071.557 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 38.5033 | 1064.8253 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 26.2542 | 1052.5762
[5 empty] | 94 | 1023.207 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 88.463 | 51.4514 | 88.463 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 51.4514 | 1074.6584 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 47.2039 | 1070.4109 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 40.2798 | 1063.4868 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.6808 | 1050.8878
[5 empty] | 96 | 1021.503 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 90.167 | 52.1273 | 90.167 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 52.1273 | 1073.6303 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 47.7619 | 1069.2649 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 40.6454 | 1062.1484 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.6964 | 1049.1994
[5 empty] | 98 | 1019.765 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 91.905 | 52.8372 | 91.905 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 52.8372 | 1072.6022 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 48.3538 | 1068.1188 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 41.045 | 1060.81 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.746 | 1047.511
[5 empty] | 100 | 1018.493 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 93.177 | 53.0811 | 93.177 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 53.0811 | 1071.5741 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 48.4797 | 1066.9727 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 40.9786 | 1059.4716 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.3296 | 1045.8226
[5 empty] | 102 | 1016.444 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 95.226 | 54.102 | 95.226 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 54.102 | 1070.546 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 49.3826 | 1065.8266 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 41.6892 | 1058.1332 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.6902 | 1044.1342
[5 empty] | 104 | 1013.288 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 98.382 | 56.2299 | 98.382 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 56.2299 | 1069.5179 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 51.3925 | 1064.6805 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 43.5067 | 1056.7947 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 29.1578 | 1042.4458
[5 empty] | 106 | 1007.843 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 103.827 | 60.6468 | 103.827 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 60.6468 | 1068.4898 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 55.6914 | 1063.5344 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 47.6133 | 1055.4563 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 32.9144 | 1040.7574
[5 empty] | 108 | 1001.282 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 110.388 | 66.1797 | 110.388 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 66.1797 | 1067.4617 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 61.1063 | 1062.3883 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 52.8359 | 1054.1179 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 37.787 | 1039.069
[5 empty] | 110 | 996.609 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.061 | 69.8246 | 115.061 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 69.8246 | 1066.4336 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 64.6333 | 1061.2423 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 56.1705 | 1052.7795 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 40.7716 | 1037.3806
[5 empty] | 112 | 992.999 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 118.671 | 72.4065 | 118.671 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 72.4065 | 1065.4055 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 67.0972 | 1060.0962 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 58.4421 | 1051.4411 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 42.6932 | 1035.6922
[5 empty] | 114 | 993.639 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 118.031 | 70.7384 | 118.031 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 70.7384 | 1064.3774 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 65.3111 | 1058.9501 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 56.4636 | 1050.1026 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 40.3648 | 1034.0038
[5 empty] | 116 | 994.611 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 117.059 | 68.7383 | 117.059 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 68.7383 | 1063.3493 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 63.193 | 1057.804 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 54.1532 | 1048.7642 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 37.7044 | 1032.3154
[5 empty] | 118 | 995.751 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.919 | 66.5702 | 115.919 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 66.5702 | 1062.3212 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 60.9069 | 1056.6579 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 51.6748 | 1047.4258 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 34.876 | 1030.627
[5 empty] | 120 | 996.479 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.191 | 64.8141 | 115.191 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 64.8141 | 1061.2931 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 59.0328 | 1055.5118 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 49.6084 | 1046.0874 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 32.4596 | 1028.9386
[5 empty] | 122 | 996.147 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.523 | 64.118 | 115.523 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 64.118 | 1060.265 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 58.2188 | 1054.3658 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 48.602 | 1044.749 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 31.1032 | 1027.2502
[5 empty] | 124 | 992.094 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 119.576 | 67.1429 | 119.576 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 67.1429 | 1059.2369 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 61.1257 | 1053.2197 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 51.3165 | 1043.4105 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 33.4679 | 1025.5619
[5 empty] | 126 | 985.623 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 126.047 | 72.5858 | 126.047 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 72.5858 | 1058.2088 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 66.4506 | 1052.0736 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 56.4491 | 1042.0721 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 38.2505 | 1023.8735
[5 empty] | 128 | 977.759 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 133.911 | 79.4217 | 133.911 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 79.4217 | 1057.1807 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 73.1685 | 1050.9275 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 62.9747 | 1040.7337 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 44.4261 | 1022.1851
[5 empty] | 130 | 969.772 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 141.898 | 86.3806 | 141.898 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 86.3806 | 1056.1526 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 80.0094 | 1049.7814 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 69.6233 | 1039.3953 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 50.7247 | 1020.4967
[5 empty] | 132 | 981.785 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 129.885 | 73.3395 | 129.885 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 73.3395 | 1055.1245 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 66.8503 | 1048.6353 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 56.2718 | 1038.0568 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 37.0233 | 1018.8083
[5 empty] | 134 | 991.458 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 120.212 | 62.6384 | 120.212 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 62.6384 | 1054.0964 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 56.0312 | 1047.4892 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 45.2604 | 1036.7184 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 25.6619 | 1017.1199
[5 empty] | 136 | 987.77 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 123.9 | 65.2983 | 123.9 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 65.2983 | 1053.0683 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 58.5732 | 1046.3432 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 47.61 | 1035.38 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.6615 | 1015.4315
[5 empty] | 138 | 982.725 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 128.945 | 69.3152 | 128.945 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 69.3152 | 1052.0402 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 62.4721 | 1045.1971 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 51.3166 | 1034.0416 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 31.0181 | 1013.7431
[5 empty] | 140 | 977.559 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 134.111 | 73.4531 | 134.111 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 73.4531 | 1051.0121 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 66.492 | 1044.051 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 55.1442 | 1032.7032 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 34.4957 | 1012.0547
[5 empty] | 142 | 975.289 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 136.381 | 74.695 | 136.381 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 74.695 | 1049.984 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 67.6159 | 1042.9049 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 56.0757 | 1031.3647 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 35.0773 | 1010.3663
[5 empty] | 144 | 973.968 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 137.702 | 74.9879 | 137.702 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 74.9879 | 1048.9559 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 67.7908 | 1041.7588 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 56.0583 | 1030.0263 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 34.7099 | 1008.6779
[5 empty] | 146 | 962.473 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 149.197 | 85.4548 | 149.197 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 85.4548 | 1047.9278 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 78.1397 | 1040.6127 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 66.2149 | 1028.6879 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 44.5165 | 1006.9895
[5 empty] | 148 | 951.285 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 160.385 | 95.6147 | 160.385 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 95.6147 | 1046.8997 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 88.1816 | 1039.4666 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 76.0645 | 1027.3495 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 54.0161 | 1005.3011
[5 empty] | 150 | 948.174 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 163.496 | 97.6976 | 163.496 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 97.6976 | 1045.8716 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 90.1466 | 1038.3206 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 77.8371 | 1026.0111 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 55.4387 | 1003.6127
[5 empty] | 152 | 944.641 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 167.029 | 100.2025 | 167.029 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 100.2025 | 1044.8435 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 92.5335 | 1037.1745 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 80.0316 | 1024.6726 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 57.2833 | 1001.9243
[5 empty] | 154 | 941.566 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 170.104 | 102.2494 | 170.104 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 102.2494 | 1043.8154 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 94.4624 | 1036.0284 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 81.7682 | 1023.3342 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 58.6699 | 1000.2359
[5 empty] | 156 | 940.942 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 170.728 | 101.8453 | 170.728 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 101.8453 | 1042.7873 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 93.9403 | 1034.8823 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 81.0538 | 1021.9958 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 57.6055 | 998.5475
[5 empty] | 158 | 939.726 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 171.944 | 102.0332 | 171.944 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 102.0332 | 1041.7592 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 94.0102 | 1033.7362 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 80.9314 | 1020.6574 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 57.1331 | 996.8591
[5 empty] | 160 | 936.738 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 174.932 | 103.9931 | 174.932 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 103.9931 | 1040.7311 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 95.8521 | 1032.5901 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 82.581 | 1019.319 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 58.4327 | 995.1707
[5 empty] | 162 | 933.65 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 178.02 | 106.053 | 178.02 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 106.053 | 1039.703 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 97.7941 | 1031.4441 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 84.3305 | 1017.9805 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 59.8323 | 993.4823
[5 empty] | 164 | 932.745 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.925 | 105.604 | 178.925 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 105.604 | 1038.349 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 97.1884 | 1029.9334 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 83.4691 | 1016.2141 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 58.5043 | 991.2493
[5 empty] | 166 | 931.696 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 179.974 | 105.299 | 179.974 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 105.299 | 1036.995 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 96.7267 | 1028.4227 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 82.7517 | 1014.4477 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 57.3203 | 989.0163
[5 empty] | 168 | 930.999 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.671 | 104.642 | 180.671 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 104.642 | 1035.641 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 95.913 | 1026.912 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 81.6823 | 1012.6813 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.7842 | 986.7832
[5 empty] | 170 | 930.885 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.785 | 103.402 | 180.785 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 103.402 | 1034.287 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 94.5163 | 1025.4013 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 80.0298 | 1010.9148 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 53.6652 | 984.5502
[5 empty] | 172 | 930.378 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 181.292 | 102.5551 | 181.292 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 102.5551 | 1032.9331 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 93.5126 | 1023.8906 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 78.7704 | 1009.1484 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 51.9391 | 982.3171
[5 empty] | 174 | 931.324 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.346 | 100.2551 | 180.346 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 100.2551 | 1031.5791 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 91.0559 | 1022.3799 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 76.058 | 1007.382 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 48.7601 | 980.0841
[5 empty] | 176 | 933.53 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.14 | 96.6951 | 178.14 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 96.6951 | 1030.2251 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 87.3392 | 1020.8692 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 72.0856 | 1005.6156 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 44.321 | 977.851
[5 empty] | 178 | 932.714 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.956 | 96.1571 | 178.956 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 96.1571 | 1028.8711 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 86.6445 | 1019.3585 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 71.1351 | 1003.8491 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 42.904 | 975.618
[5 empty] | 180 | 928.311 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.359 | 99.2061 | 183.359 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 99.2061 | 1027.5171 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 89.5368 | 1017.8478 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 73.7717 | 1002.0827 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 45.0739 | 973.3849
[5 empty] | 182 | 924.179 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 187.491 | 101.9842 | 187.491 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 101.9842 | 1026.1632 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 92.1581 | 1016.3371 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 76.1373 | 1000.3163 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 46.9729 | 971.1519
[5 empty] | 184 | 928.398 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.272 | 96.4112 | 183.272 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 96.4112 | 1024.8092 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 86.4284 | 1014.8264 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 70.1519 | 998.5499 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 40.5209 | 968.9189
[5 empty] | 186 | 930.866 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.804 | 92.5892 | 180.804 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.5892 | 1023.4552 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 82.4497 | 1013.3157 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 65.9174 | 996.7834 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 35.8198 | 966.6858
[5 empty] | 188 | 928.411 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.259 | 93.6902 | 183.259 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 93.6902 | 1022.1012 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 83.394 | 1011.805 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 66.606 | 995.017 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 36.0418 | 964.4528
[5 empty] | 190 | 927.849 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.821 | 92.8982 | 183.821 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.8982 | 1020.7472 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 82.4453 | 1010.2943 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 65.4016 | 993.2506 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 34.3707 | 962.2197
[5 empty] | 192 | 926.71 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 184.96 | 92.6832 | 184.96 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.6832 | 1019.3932 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 82.0736 | 1008.7836 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 64.7742 | 991.4842 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 33.2767 | 959.9867
[5 empty] | 194 | 926.201 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 185.469 | 91.8383 | 185.469 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 91.8383 | 1018.0393 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 81.0719 | 1007.2729 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 63.5167 | 989.7177 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 31.5526 | 957.7536
[5 empty] | 196 | 924.509 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 187.161 | 92.1763 | 187.161 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.1763 | 1016.6853 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 81.2532 | 1005.7622 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 63.4423 | 987.9513 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 31.0116 | 955.5206
[5 empty] | 198 | 923.417 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 188.253 | 91.9143 | 188.253 | 11.2952 | 996509.3057 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 91.9143 | 1015.3313 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 80.8345 | 1004.2515 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 62.7679 | 986.1849 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 29.8705 | 953.2875
[5 empty] | 200 | 923.011 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 188.659 | 90.9663 | 188.659 | 11.3195 | 998644.849 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 90.9663 | 1013.9773 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.7298 | 1002.7408 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 61.4075 | 984.4185 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 28.0435 | 951.0545
[5 empty] | 202 | 921.969 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 189.701 | 90.6543 | 189.701 | 11.3821 | 1004125.4583 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 90.6543 | 1012.6233 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.2611 | 1001.2301 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 60.683 | 982.652 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 26.8525 | 948.8215
[5 empty] | 204 | 920.661 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 191.009 | 90.6084 | 191.009 | 11.4605 | 1011004.6025 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 90.6084 | 1011.2694 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.0584 | 999.7194 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 60.2246 | 980.8856 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 25.9274 | 946.5884
[5 empty] | 206 | 920.243 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 191.427 | 89.6724 | 191.427 | 11.4856 | 1013202.8554 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 89.6724 | 1009.9154 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 77.9657 | 998.2087 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 58.8762 | 979.1192 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 24.1124 | 944.3554
[5 empty] | 208 | 919.297 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 192.373 | 89.2644 | 192.373 | 11.5424 | 1018177.6195 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 89.2644 | 1008.5614 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 77.401 | 996.698 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 58.0558 | 977.3528 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 22.8253 | 942.1223
[5 empty] | 210 | 917.533 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 194.137 | 89.6744 | 194.137 | 11.6482 | 1027453.1808 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 89.6744 | 1007.2074 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 77.6543 | 995.1873 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 58.0533 | 975.5863 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 22.3563 | 939.8893
[5 empty] | 212 | 917.684 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 193.986 | 88.1694 | 193.986 | 11.6392 | 1026659.2276 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 88.1694 | 1005.8534 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 75.9926 | 993.6766 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 56.1359 | 973.8199 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 19.9722 | 937.6562
[5 empty] | 214 | 915.724 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 195.946 | 88.7754 | 195.946 | 11.7568 | 1036964.2159 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 88.7754 | 1004.4994 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 76.4419 | 992.1659 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 56.3295 | 972.0535 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 19.6992 | 935.4232
[5 empty] | 216 | 915.73 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 195.94 | 87.4155 | 195.94 | 11.7564 | 1036932.6721 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 87.4155 | 1003.1455 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 74.9252 | 990.6552 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 54.5571 | 970.2871 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 17.4601 | 933.1901
[5 empty] | 218 | 915.584 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 196.086 | 86.2075 | 196.086 | 11.7652 | 1037700.2343 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 86.2075 | 1001.7915 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 73.5605 | 989.1445 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 52.9366 | 968.5206 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 15.3731 | 930.9571
[5 empty] | 220 | 915.444 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 196.226 | 84.9935 | 196.226 | 11.7736 | 1038436.2457 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 84.9935 | 1000.4375 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 72.1898 | 987.6338 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 51.3102 | 966.7542 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 13.2801 | 928.7241
[5 empty] | 222 | 913.52 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 198.15 | 85.5635 | 198.15 | 11.889 | 1048550.4405 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 85.5635 | 999.0835 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 72.6031 | 986.1231 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 51.4678 | 964.9878 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 12.971 | 926.491
[5 empty] | 224 | 912.524 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 199.146 | 85.2055 | 199.146 | 11.9488 | 1053785.7546 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 85.2055 | 997.7295 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 72.0884 | 984.6124 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 50.6974 | 963.2214 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 11.734 | 924.258
[5 empty] | 226 | 912.565 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | 199.105 | 84.3726 | 199.105 | 13.2737 | 1300704.0144 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 84.3726 | 996.9376 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 71.1653 | 983.7303 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 49.6275 | 962.1925 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 10.3977 | 922.9627
|  |  |  | Reservoir | 228 | 913.484 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 10 | 130 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 120 | 10 | 1043.484 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 120 | 130 | 1043.484 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 120 | 130 | 1043.484 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 120 | 130 | 1043.484
[5 empty] | 230 | 913.545 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 269.451 | 269.3964 | 19.7557 | 2124456.501 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 269.451 | 1182.996 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 269.3964 | 1182.9414 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 269.3075 | 1182.8525 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 269.147 | 1182.692
[5 empty] | 232 | 914.546 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 267.9621 | 267.8527 | 19.6425 | 2112393.122 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 267.9621 | 1182.5081 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 267.8527 | 1182.3987 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 267.675 | 1182.221 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 267.3539 | 1181.8999
[5 empty] | 234 | 918.285 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 263.7351 | 263.5711 | 19.3285 | 2078925.8204 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 263.7351 | 1182.0201 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 263.5711 | 1181.8561 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 263.3045 | 1181.5895 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 262.8229 | 1181.1079
[5 empty] | 236 | 919.357 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 262.1751 | 261.9565 | 19.2101 | 2066302.5605 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 262.1751 | 1181.5321 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 261.9565 | 1181.3135 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 261.601 | 1180.958 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 260.9588 | 1180.3158
[5 empty] | 238 | 918.649 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 262.3951 | 262.1218 | 19.2223 | 2067595.4923 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 262.3951 | 1181.0441 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 262.1218 | 1180.7708 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 261.6775 | 1180.3265 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 260.8748 | 1179.5238
[5 empty] | 240 | 922.974 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 257.5822 | 257.2542 | 18.8653 | 2029532.1749 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 257.5822 | 1180.5562 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 257.2542 | 1180.2282 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 256.721 | 1179.695 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 255.7577 | 1178.7317
[5 empty] | 242 | 927.375 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 252.6932 | 252.3106 | 18.5028 | 1990861.6963 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 252.6932 | 1180.0682 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 252.3106 | 1179.6856 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 251.6885 | 1179.0635 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 250.5647 | 1177.9397
[5 empty] | 244 | 929.253 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 250.3272 | 249.89 | 18.3253 | 1971922.111 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 250.3272 | 1179.5802 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 249.89 | 1179.143 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 249.179 | 1178.432 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 247.8946 | 1177.1476
[5 empty] | 246 | 930.863 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 248.2293 | 247.7373 | 18.1674 | 1955076.8099 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 248.2293 | 1179.0923 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 247.7373 | 1178.6003 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 246.9375 | 1177.8005 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 245.4926 | 1176.3556
[5 empty] | 248 | 931.924 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 246.6803 | 246.1337 | 18.0498 | 1942526.0831 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 246.6803 | 1178.6043 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 246.1337 | 1178.0577 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 245.245 | 1177.169 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 243.6395 | 1175.5635
[5 empty] | 250 | 936.722 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 241.3943 | 240.7931 | 17.6582 | 1900718.089 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 241.3943 | 1178.1163 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 240.7931 | 1177.5151 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 239.8155 | 1176.5375 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 238.0495 | 1174.7715
[5 empty] | 252 | 941.777 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 235.8513 | 235.1954 | 17.2477 | 1856881.9842 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 235.8513 | 1177.6283 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 235.1954 | 1176.9724 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 234.129 | 1175.906 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 232.2024 | 1173.9794
[5 empty] | 254 | 948.143 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 228.9974 | 228.2868 | 16.741 | 1802756.2719 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 228.9974 | 1177.1404 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 228.2868 | 1176.4298 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 227.1315 | 1175.2745 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 225.0444 | 1173.1874
[5 empty] | 256 | 955.417 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 221.2354 | 220.4702 | 16.1678 | 1741486.2968 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 221.2354 | 1176.6524 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 220.4702 | 1175.8872 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 219.226 | 1174.643 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 216.9783 | 1172.3953
[5 empty] | 258 | 962.7 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 213.4644 | 212.6445 | 15.5939 | 1680113.3067 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 213.4644 | 1176.1644 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 212.6445 | 1175.3445 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 211.3115 | 1174.0115 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 208.9033 | 1171.6033
[5 empty] | 260 | 969.281 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 206.3955 | 205.5209 | 15.0715 | 1624217.5481 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 206.3955 | 1175.6765 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 205.5209 | 1174.8019 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 204.099 | 1173.38 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 201.5302 | 1170.8112
[5 empty] | 262 | 980.284 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 194.9045 | 193.9753 | 14.2249 | 1533567.2726 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 194.9045 | 1175.1885 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 193.9753 | 1174.2593 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 192.4645 | 1172.7485 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 189.7352 | 1170.0192
[5 empty] | 264 | 986.551 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 188.1495 | 187.1657 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 188.1495 | 1174.7005 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 187.1657 | 1173.7167 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 185.566 | 1172.117 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 182.6761 | 1169.2271
[5 empty] | 266 | 989.198 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 185.0146 | 183.976 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 185.0146 | 1174.2126 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 183.976 | 1173.174 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 182.2875 | 1171.4855 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 179.2371 | 1168.4351
[5 empty] | 268 | 994.39 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 179.3346 | 178.2414 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 179.3346 | 1173.7246 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 178.2414 | 1172.6314 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 176.464 | 1170.854 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 173.253 | 1167.643
[5 empty] | 270 | 999.917 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 173.3196 | 172.1718 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 173.3196 | 1173.2366 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 172.1718 | 1172.0888 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 170.3055 | 1170.2225 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 166.934 | 1166.851
[5 empty] | 272 | 1004.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 168.1256 | 166.9231 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 168.1256 | 1172.7486 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 166.9231 | 1171.5461 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 164.968 | 1169.591 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 161.4359 | 1166.0589 | 1165.2669
[5 empty] | 274 | 1008.819 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 163.4417 | 162.1845 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 163.4417 | 1172.2607 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 162.1845 | 1171.0035 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 160.1405 | 1168.9595 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 156.4479 | 1165.2669 | 0
[5 empty] | 276 | 1007.834 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 163.9387 | 162.6269 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 163.9387 | 1171.7727 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 162.6269 | 1170.4609 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 160.494 | 1168.328 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 156.6408 | 1164.4748
[5 empty] | 278 | 1005.626 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 165.6587 | 164.2922 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 165.6587 | 1171.2847 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 164.2922 | 1169.9182 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 162.0705 | 1167.6965 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 158.0568 | 1163.6828
[5 empty] | 280 | 1001.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 169.1738 | 167.7526 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 169.1738 | 1170.7968 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 167.7526 | 1169.3756 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 165.442 | 1167.065 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 161.2677 | 1162.8907
[5 empty] | 282 | 1004.052 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 166.2568 | 164.781 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 166.2568 | 1170.3088 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 164.781 | 1168.833 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 162.3815 | 1166.4335 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 158.0467 | 1162.0987
[5 empty] | 284 | 1010.797 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 159.0238 | 157.4934 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 159.0238 | 1169.8208 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 157.4934 | 1168.2904 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 155.005 | 1165.802 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 150.5096 | 1161.3066
[5 empty] | 286 | 1014.67 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 154.6628 | 153.0777 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 154.6628 | 1169.3328 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 153.0777 | 1167.7477 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 150.5005 | 1165.1705 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 145.8446 | 1160.5146
[5 empty] | 288 | 1017.319 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 151.5259 | 149.8861 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 151.5259 | 1168.8449 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 149.8861 | 1167.2051 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 147.22 | 1164.539 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 142.4035 | 1159.7225
[5 empty] | 290 | 1027.459 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 140.8979 | 139.2035 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 140.8979 | 1168.3569 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 139.2035 | 1166.6625 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 136.4485 | 1163.9075 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 131.4715 | 1158.9305
[5 empty] | 292 | 1031.99 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 135.8789 | 134.1298 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 135.8789 | 1167.8689 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 134.1298 | 1166.1198 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 131.286 | 1163.276 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 126.1484 | 1158.1384
[5 empty] | 294 | 1036.254 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 131.127 | 129.3232 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 131.127 | 1167.381 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 129.3232 | 1165.5772 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 126.3905 | 1162.6445 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 121.0924 | 1157.3464
[5 empty] | 296 | 1040.127 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 126.766 | 124.9076 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 126.766 | 1166.893 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 124.9076 | 1165.0346 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 121.886 | 1162.013 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 116.4273 | 1156.5543
[5 empty] | 298 | 1044.396 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 122.009 | 120.0959 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 122.009 | 1166.405 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 120.0959 | 1164.4919 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 116.9855 | 1161.3815 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 111.3663 | 1155.7623
[5 empty] | 300 | 1051.339 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 114.578 | 112.6103 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 114.578 | 1165.917 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 112.6103 | 1163.9493 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 109.411 | 1160.75 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 103.6312 | 1154.9702
[5 empty] | 302 | 1060.955 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 104.4741 | 102.4517 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 104.4741 | 1165.4291 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 102.4517 | 1163.4067 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 99.1635 | 1160.1185 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 93.2232 | 1154.1782
[5 empty] | 304 | 1070.227 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 94.7141 | 92.637 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 94.7141 | 1164.9411 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 92.637 | 1162.864 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 89.26 | 1159.487 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 83.1591 | 1153.3861
[5 empty] | 306 | 1072.691 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 91.7621 | 89.6304 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 91.7621 | 1164.4531 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 89.6304 | 1162.3214 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 86.1645 | 1158.8555 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 79.9031 | 1152.5941
[5 empty] | 308 | 1076.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 87.4622 | 85.2758 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 87.4622 | 1163.9652 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 85.2758 | 1161.7788 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 81.721 | 1158.224 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 75.299 | 1151.802
[5 empty] | 310 | 1083.996 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 79.4812 | 77.2402 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 79.4812 | 1163.4772 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 77.2402 | 1161.2362 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 73.5965 | 1157.5925 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 67.014 | 1151.01
[5 empty] | 312 | 1097.188 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 65.8012 | 63.5055 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 65.8012 | 1162.9892 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 63.5055 | 1160.6935 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 59.773 | 1156.961 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 53.0299 | 1150.2179
[5 empty] | 314 | 1103.545 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 58.9563 | 56.6059 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 58.9563 | 1162.5013 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 56.6059 | 1160.1509 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 52.7845 | 1156.3295 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 45.8809 | 1149.4259
[5 empty] | 316 | 1105.174 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 56.8393 | 54.4343 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 56.8393 | 1162.0133 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 54.4343 | 1159.6083 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 50.524 | 1155.698 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 43.4598 | 1148.6338
[5 empty] | 318 | 1111.657 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 49.8683 | 47.4086 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 49.8683 | 1161.5253 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 47.4086 | 1159.0656 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 43.4095 | 1155.0665 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 36.1848 | 1147.8418
[5 empty] | 320 | 1122.935 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 38.1023 | 35.588 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 38.1023 | 1161.0373 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 35.588 | 1158.523 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 31.5 | 1154.435 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 24.1147 | 1147.0497
[5 empty] | 322 | 1128.197 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 32.3524 | 29.7834 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 32.3524 | 1160.5494 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 29.7834 | 1157.9804 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 25.6065 | 1153.8035 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 18.0607 | 1146.2577
[5 empty] | 324 | 1132.561 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 27.5004 | 24.8767 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 27.5004 | 1160.0614 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 24.8767 | 1157.4377 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 20.611 | 1153.172 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 12.9046 | 1145.4656
[5 empty] | 326 | 1131.854 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 27.7194 | 25.0411 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 27.7194 | 1159.5734 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 25.0411 | 1156.8951 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 20.6865 | 1152.5405 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 12.8196 | 1144.6736
[5 empty] | 328 | 1133.338 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 25.7475 | 23.0145 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 25.7475 | 1159.0855 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 23.0145 | 1156.3525 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 18.571 | 1151.909 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 10.5435 | 1143.8815
|  |  |  | Reservoir | 330 | 1136.405 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 22.1925 | 19.4049 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 22.1925 | 1158.5975 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 19.4049 | 1155.8099 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 14.8725 | 1151.2775 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 6.6845 | 1143.0895
[5 empty] | 332 | 1128.709 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 29.4005 | 26.5582 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 29.4005 | 1158.1095 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 26.5582 | 1155.2672 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 21.937 | 1150.646 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 13.5884 | 1142.2974
[5 empty] | 334 | 1120.713 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 36.9085 | 34.0116 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.035283 | 0.48797 | 0 | 36.9085 | 1157.6215 | 0.0094904 | 0.50735 | 0.035283 | 0.54263 | 0 | 34.0116 | 1154.7246 | 0.011153 | 0.59622 | 0.035283 | 0.6315 | 0 | 29.3015 | 1150.0145 | 0.014105 | 0.75677 | 0.035283 | 0.79205 | 0 | 20.7924 | 1141.5054
[5 empty] | 336 | 1115.226 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 41.0416 | 37.9879 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 41.0416 | 1156.2676 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 37.9879 | 1153.2139 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 33.0221 | 1148.2481 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 24.0463 | 1139.2723
[5 empty] | 338 | 1108.709 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 46.2046 | 42.9942 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 46.2046 | 1154.9136 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 42.9942 | 1151.7032 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 37.7726 | 1146.4816 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 28.3303 | 1137.0393
[5 empty] | 340 | 1102.499 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 51.0606 | 47.6935 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 51.0606 | 1153.5596 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 47.6935 | 1150.1925 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 42.2162 | 1144.7152 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 32.3072 | 1134.8062
[5 empty] | 342 | 1096.349 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 55.8566 | 52.3328 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 55.8566 | 1152.2056 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 52.3328 | 1148.6818 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 46.5998 | 1142.9488 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 36.2242 | 1132.5732
[5 empty] | 344 | 1090.39 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 60.4616 | 56.7811 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 60.4616 | 1150.8516 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 56.7811 | 1147.1711 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 50.7924 | 1141.1824 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 39.9502 | 1130.3402
[5 empty] | 346 | 1087.765 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 61.7327 | 57.8954 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 61.7327 | 1149.4977 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 57.8954 | 1145.6604 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 51.6509 | 1139.4159 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 40.3421 | 1128.1071
[5 empty] | 348 | 1084.661 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 63.4827 | 59.4887 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 63.4827 | 1148.1437 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 59.4887 | 1144.1497 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 52.9885 | 1137.6495 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 41.2131 | 1125.8741
[5 empty] | 350 | 1081.662 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 65.1277 | 60.977 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 65.1277 | 1146.7897 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 60.977 | 1142.639 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 54.2211 | 1135.8831 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 41.979 | 1123.641
[5 empty] | 352 | 1076.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 68.5637 | 64.2563 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 68.5637 | 1145.4357 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 64.2563 | 1141.1283 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 57.2447 | 1134.1167 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 44.536 | 1121.408
[5 empty] | 354 | 1070.898 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 73.1837 | 68.7196 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 73.1837 | 1144.0817 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 68.7196 | 1139.6176 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 61.4522 | 1132.3502 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 48.2769 | 1119.1749
[5 empty] | 356 | 1065.018 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 77.7097 | 73.0889 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 77.7097 | 1142.7277 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 73.0889 | 1138.1069 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 65.5658 | 1130.5838 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 51.9239 | 1116.9419
[5 empty] | 358 | 1059.58 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 81.7938 | 77.0162 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 81.7938 | 1141.3738 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 77.0162 | 1136.5962 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 69.2374 | 1128.8174 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.1288 | 1114.7088
[5 empty] | 360 | 1055.284 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 84.7358 | 79.8015 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 84.7358 | 1140.0198 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.8015 | 1135.0855 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 71.767 | 1127.051 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 57.1918 | 1112.4758
[5 empty] | 362 | 1050.886 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 87.7798 | 82.6888 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 87.7798 | 1138.6658 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 82.6888 | 1133.5748 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 74.3985 | 1125.2845 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 59.3568 | 1110.2428
[5 empty] | 364 | 1052.647 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 84.6648 | 79.4171 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 84.6648 | 1137.3118 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.4171 | 1132.0641 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 70.8711 | 1123.5181 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.3627 | 1108.0097
[5 empty] | 366 | 1051.117 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 84.8408 | 79.4364 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 84.8408 | 1135.9578 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.4364 | 1130.5534 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 70.6347 | 1121.7517 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 54.6597 | 1105.7767
[5 empty] | 368 | 1048.266 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 86.3378 | 80.7767 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 86.3378 | 1134.6038 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 80.7767 | 1129.0427 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 71.7193 | 1119.9853 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.2776 | 1103.5436
[5 empty] | 370 | 1040.172 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 93.0779 | 87.36 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 93.0779 | 1133.2499 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 87.36 | 1127.532 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 78.0468 | 1118.2188 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 61.1386 | 1101.3106
[5 empty] | 372 | 1033.483 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 98.4129 | 92.5383 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 98.4129 | 1131.8959 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 92.5383 | 1126.0213 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 82.9694 | 1116.4524 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 65.5945 | 1099.0775
[5 empty] | 374 | 1030.95 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 99.5919 | 93.5606 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 99.5919 | 1130.5419 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 93.5606 | 1124.5106 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 83.736 | 1114.686 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 65.8945 | 1096.8445
[5 empty] | 376 | 1032.263 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 96.9249 | 90.7369 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 96.9249 | 1129.1879 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 90.7369 | 1122.9999 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 80.6566 | 1112.9196 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 62.3484 | 1094.6114
[5 empty] | 378 | 1031.391 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 96.4429 | 90.0982 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 96.4429 | 1127.8339 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 90.0982 | 1121.4892 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 79.7621 | 1111.1531 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 60.9874 | 1092.3784
[5 empty] | 380 | 1025.791 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 100.689 | 94.1876 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 100.689 | 1126.48 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 94.1876 | 1119.9786 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 83.5957 | 1109.3867 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 64.3544 | 1090.1454
[5 empty] | 382 | 1020.911 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 104.215 | 97.5569 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 104.215 | 1125.126 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 97.5569 | 1118.4679 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 86.7093 | 1107.6203 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 67.0013 | 1087.9123
[5 empty] | 384 | 1015.65 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 108.122 | 101.3072 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 108.122 | 1123.772 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 101.3072 | 1116.9572 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 90.2039 | 1105.8539 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 70.0293 | 1085.6793
[5 empty] | 386 | 1012.139 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 110.279 | 103.3075 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 110.279 | 1122.418 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 103.3075 | 1115.4465 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 91.9484 | 1104.0874 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 71.3072 | 1083.4462
[5 empty] | 388 | 1010.472 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 110.592 | 103.4638 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 110.592 | 1121.064 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 103.4638 | 1113.9358 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 91.849 | 1102.321 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 70.7412 | 1081.2132
[5 empty] | 390 | 1005.401 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 114.309 | 107.0241 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 114.309 | 1119.71 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 107.0241 | 1112.4251 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 95.1536 | 1100.5546 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 73.5791 | 1078.9801
[5 empty] | 392 | 996.666 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 121.6901 | 114.2484 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 121.6901 | 1118.3561 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 114.2484 | 1110.9144 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 102.1222 | 1098.7882 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 80.0811 | 1076.7471
[5 empty] | 394 | 991.35 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 125.6521 | 118.0537 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 125.6521 | 1117.0021 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 118.0537 | 1109.4037 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 105.6717 | 1097.0217 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 83.164 | 1074.514
[5 empty] | 396 | 990.486 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 125.1621 | 117.407 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 125.1621 | 1115.6481 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 117.407 | 1107.893 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 104.7693 | 1095.2553 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 81.795 | 1072.281
[5 empty] | 398 | 992.761 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 121.5331 | 113.6213 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 121.5331 | 1114.2941 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 113.6213 | 1106.3823 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 100.7279 | 1093.4889 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 77.287 | 1070.048
[5 empty] | 400 | 999.077 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 113.8631 | 105.7946 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 113.8631 | 1112.9401 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 105.7946 | 1104.8716 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 92.6455 | 1091.7225 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 68.7379 | 1067.8149
[5 empty] | 402 | 1001.8 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 109.7862 | 101.5609 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 109.7862 | 1111.5862 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 101.5609 | 1103.3609 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 88.156 | 1089.956 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 63.7819 | 1065.5819
[5 empty] | 404 | 1002.224 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 108.0082 | 99.6262 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 108.0082 | 1110.2322 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 99.6262 | 1101.8502 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 85.9656 | 1088.1896 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 61.1248 | 1063.3488
[5 empty] | 406 | 1002.003 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 106.8752 | 98.3365 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 106.8752 | 1108.8782 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 98.3365 | 1100.3395 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 84.4202 | 1086.4232 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 59.1128 | 1061.1158
[5 empty] | 408 | 1003.596 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 103.9282 | 95.2328 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 103.9282 | 1107.5242 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 95.2328 | 1098.8288 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 81.0608 | 1084.6568 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.2867 | 1058.8827
[5 empty] | 410 | 994.111 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 112.0592 | 103.2071 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 112.0592 | 1106.1702 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 103.2071 | 1097.3181 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 88.7793 | 1082.8903 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 62.5387 | 1056.6497
[5 empty] | 412 | 983.925 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 120.8912 | 111.8824 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 120.8912 | 1104.8162 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 111.8824 | 1095.8074 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 97.1989 | 1081.1239 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 70.4916 | 1054.4166
[5 empty] | 414 | 972.347 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 131.1153 | 121.9497 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 131.1153 | 1103.4623 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 121.9497 | 1094.2967 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 107.0105 | 1079.3575 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 79.8366 | 1052.1836
[5 empty] | 416 | 963.901 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 138.2073 | 128.885 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 138.2073 | 1102.1083 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 128.885 | 1092.786 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 113.6901 | 1077.5911 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 86.0495 | 1049.9505
[5 empty] | 418 | 963.258 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 137.4963 | 128.0173 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 137.4963 | 1100.7543 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 128.0173 | 1091.2753 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 112.5666 | 1075.8246 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 84.4595 | 1047.7175
[5 empty] | 420 | 965.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 133.5283 | 123.8926 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 133.5283 | 1099.4003 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 123.8926 | 1089.7646 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 108.1862 | 1074.0582 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 79.6125 | 1045.4845
[5 empty] | 422 | 966.177 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 131.8693 | 122.0769 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 131.8693 | 1098.0463 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 122.0769 | 1088.2539 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 106.1148 | 1072.2918 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 77.0744 | 1043.2514
[5 empty] | 424 | 973.825 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 122.8674 | 112.9182 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 122.8674 | 1096.6924 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 112.9182 | 1086.7432 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 96.7004 | 1070.5254 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 67.1934 | 1041.0184
[5 empty] | 426 | 983.972 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 111.3664 | 101.2605 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 111.3664 | 1095.3384 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 101.2605 | 1085.2325 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 84.7869 | 1068.7589 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 54.8133 | 1038.7853
[5 empty] | 428 | 994.096 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 99.8884 | 89.6258 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 99.8884 | 1093.9844 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 89.6258 | 1083.7218 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 72.8965 | 1066.9925 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 42.4563 | 1036.5523
[5 empty] | 430 | 991.695 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 100.9354 | 90.5161 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 100.9354 | 1092.6304 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 90.5161 | 1082.2111 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 73.5311 | 1065.2261 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 42.6242 | 1034.3192
[5 empty] | 432 | 984.933 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 106.3434 | 95.7674 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 106.3434 | 1091.2764 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 95.7674 | 1080.7004 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 78.5267 | 1063.4597 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 47.1532 | 1032.0862
[5 empty] | 434 | 974.509 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 115.4134 | 104.6807 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 115.4134 | 1089.9224 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 104.6807 | 1079.1897 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 87.1842 | 1061.6932 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.3441 | 1029.8531
[5 empty] | 436 | 966.698 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 121.8705 | 110.981 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 121.8705 | 1088.5685 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 110.981 | 1077.679 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 93.2288 | 1059.9268 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 60.9221 | 1027.6201
[5 empty] | 438 | 963.618 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 123.5965 | 112.5503 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 123.5965 | 1087.2145 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 112.5503 | 1076.1683 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 94.5424 | 1058.1604 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 61.7691 | 1025.3871
[5 empty] | 440 | 957.803 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 128.0575 | 116.8546 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 128.0575 | 1085.8605 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 116.8546 | 1074.6576 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 98.591 | 1056.394 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 65.351 | 1023.154
[5 empty] | 442 | 954.277 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 130.2295 | 118.8699 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 130.2295 | 1084.5065 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 118.8699 | 1073.1469 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 100.3505 | 1054.6275 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 66.644 | 1020.921
[5 empty] | 444 | 947.182 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 135.9705 | 124.4542 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 135.9705 | 1083.1525 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 124.4542 | 1071.6362 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 105.6791 | 1052.8611 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 71.5059 | 1018.6879
[5 empty] | 446 | 938.045 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 143.7536 | 132.0805 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 143.7536 | 1081.7986 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 132.0805 | 1070.1255 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 113.0497 | 1051.0947 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 78.4099 | 1016.4549
[5 empty] | 448 | 930.871 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 149.5736 | 137.7438 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 149.5736 | 1080.4446 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 137.7438 | 1068.6148 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 118.4573 | 1049.3283 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 83.3508 | 1014.2218
[5 empty] | 450 | 926.391 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 152.6996 | 140.7131 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 152.6996 | 1079.0906 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 140.7131 | 1067.1041 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 121.1708 | 1047.5618 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 85.5978 | 1011.9888
[5 empty] | 452 | 918.344 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 159.3926 | 147.2494 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 159.3926 | 1077.7366 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 147.2494 | 1065.5934 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 127.4514 | 1045.7954 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 91.4117 | 1009.7557
[5 empty] | 454 | 911.505 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 164.8776 | 152.5777 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 164.8776 | 1076.3826 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 152.5777 | 1064.0827 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 132.524 | 1044.029 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 96.0177 | 1007.5227
[5 empty] | 456 | 903.61 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 171.4186 | 158.962 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 171.4186 | 1075.0286 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 158.962 | 1062.572 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 138.6526 | 1042.2626 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 101.6797 | 1005.2897
[5 empty] | 458 | 900.63 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 173.0447 | 160.4313 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 173.0447 | 1073.6747 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 160.4313 | 1061.0613 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 139.8661 | 1040.4961 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 102.4266 | 1003.0566
[5 empty] | 460 | 904.066 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 168.2547 | 155.4847 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 168.2547 | 1072.3207 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 155.4847 | 1059.5507 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 134.6637 | 1038.7297 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 96.7576 | 1000.8236
[5 empty] | 462 | 915.092 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 155.8747 | 142.948 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 155.8747 | 1070.9667 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 142.948 | 1058.04 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 121.8713 | 1036.9633 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 83.4985 | 998.5905
[5 empty] | 464 | 905.556 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 164.0567 | 150.9733 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 164.0567 | 1069.6127 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 150.9733 | 1056.5293 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 129.6409 | 1035.1969 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 90.8015 | 996.3575
[5 empty] | 466 | 905.271 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 162.9877 | 149.7476 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 162.9877 | 1068.2587 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 149.7476 | 1055.0186 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 128.1594 | 1033.4304 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 88.8534 | 994.1244
[5 empty] | 468 | 901.918 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 164.9868 | 151.5899 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 164.9868 | 1066.9048 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 151.5899 | 1053.5079 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 129.746 | 1031.664 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 89.9734 | 991.8914
[5 empty] | 470 | 895.651 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 169.8998 | 156.3462 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 169.8998 | 1065.5508 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 156.3462 | 1051.9972 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 134.2466 | 1029.8976 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 94.0073 | 989.6583
[5 empty] | 472 | 892.304 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 171.8928 | 158.1825 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 171.8928 | 1064.1968 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 158.1825 | 1050.4865 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 135.8272 | 1028.1312 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 95.1213 | 987.4253
[5 empty] | 474 | 895.279 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 167.5638 | 153.6968 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 167.5638 | 1062.8428 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 153.6968 | 1048.9758 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 131.0857 | 1026.3647 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 89.9133 | 985.1923
[5 empty] | 476 | 896.818 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 164.6708 | 150.6471 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 164.6708 | 1061.4888 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 150.6471 | 1047.4651 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 127.7803 | 1024.5983 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 86.1412 | 982.9592
[5 empty] | 478 | 909.921 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 148.1352 | 133.7031 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 148.1352 | 1058.0562 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 133.7031 | 1043.6241 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 110.1677 | 1020.0887 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 67.2963 | 977.2173
[5 empty] | 480 | 926.295 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 128.3286 | 113.4881 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 128.3286 | 1054.6236 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 113.4881 | 1039.7831 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 89.2841 | 1015.5791 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 45.1803 | 971.4753
[5 empty] | 482 | 924.888 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 126.303 | 111.0541 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 126.303 | 1051.191 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 111.0541 | 1035.9421 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 86.1814 | 1011.0694 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 40.8454 | 965.7334
[5 empty] | 484 | 919.044 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 128.7144 | 113.0572 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 128.7144 | 1047.7584 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 113.0572 | 1032.1012 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 87.5158 | 1006.5598 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 40.9475 | 959.9915
[5 empty] | 486 | 911.164 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 133.1618 | 117.0962 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 133.1618 | 1044.3258 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 117.0962 | 1028.2602 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 90.8862 | 1002.0502 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 43.0855 | 954.2495
[5 empty] | 488 | 903.893 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 137.0002 | 120.5262 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 137.0002 | 1040.8932 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 120.5262 | 1024.4192 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 93.6476 | 997.5406 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 44.6146 | 948.5076
[5 empty] | 490 | 901.953 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 135.5075 | 118.6252 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 135.5075 | 1037.4605 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 118.6252 | 1020.5782 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 91.078 | 993.031 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 40.8127 | 942.7657
[5 empty] | 492 | 900.198 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 133.8299 | 116.5393 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 133.8299 | 1034.0279 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 116.5393 | 1016.7373 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 88.3233 | 988.5213 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 36.8257 | 937.0237
[5 empty] | 494 | 904.177 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 126.4183 | 108.7193 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 126.4183 | 1030.5953 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 108.7193 | 1012.8963 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 79.8347 | 984.0117 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 27.1048 | 931.2818
[5 empty] | 496 | 912.253 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 114.9097 | 96.8023 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 114.9097 | 1027.1627 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 96.8023 | 1009.0553 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 67.2491 | 979.5021 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 13.2868 | 925.5398
[5 empty] | 498 | 915.297 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 108.4331 | 89.9173 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 108.4331 | 1023.7301 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 89.9173 | 1005.2143 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 59.6955 | 974.9925 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 4.5009 | 919.7979
|  |  |  | Reservoir | 500 | 919.629 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 10 | 10 | 10 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 10 | 929.629 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 10 | 929.629 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 10 | 929.629 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 10 | 929.629
[15 empty] | Total Steel Mass (kg): | 286817693.8792