## Cost Estimates
Air Valve, Scour Valve & Isolating Budget |  |  |  | Steel Pipe Prices |  | Pump Station Costs - DWA 2003 Escalated to 2010 |  | Electricity Costs | Pula | Rand | Reservoir Costing |  | Minor Loss - k | 150 | Pipe Trench Excavation & Back Fill
Pipe Diameter (mm) | Civil Rate/m | Mechanical Rate/m | Total R/m | Coating Cost Per m2 | 200 | PS Capacity kW | Cost R/kW | Fixed Charge Per Month | 26.09 | 28.699 | Reservoir (incl. earthowrks and lining) per m3 | 80 |  |  | Excavation Cost (R/m3) | 50
500 | 40 | 70 | 110 | Steel Pipe Cost Per Ton | 17.5 | 100 | 30227.6622 | Energy Charge Per kWh | 0.4096 | 0.45056 |  |  | Friction Factors |  | Bedding and Cradle Fill (R/m3) | 165
600 | 40 | 80 | 120 | Delivery Cost Per m | 85 | 200 | 25032.9622 | [5 empty] | Ks (mm) - New | 0.03 | Main Fill (R/m3) | 55
700 | 40 | 100 | 140 | Laying and Joining 20% of Pipe Price |  | 300 | 22423.6676 | [5 empty] | Ks (mm) - Average | 0.06 | Spoil (R/m3) | 45
800 | 40 | 140 | 180 |  |  | 400 | 20740.1478 | [5 empty] | Ks (mm) - Old | 0.15
900 | 40 | 190 | 230 |  |  | 500 | 19523.2464 | [5 empty] | Ks (mm) - Biofilm | 0.5
1000 | 40 | 250 | 290 |  |  | 600 | 18582.6012
1100 | 40 | 360 | 400 |  |  | 700 | 17823.054
1200 | 50 | 460 | 510 |  |  | 800 | 17190.3824
1300 | 50 | 480 | 530 |  |  | 900 | 16651.2418
1400 | 50 | 500 | 550 |  |  | 1000 | 16183.5318
1500 | 50 | 530 | 580 |  |  | 2000 | 13420.2993
1600 | 60 | 560 | 620 |  |  | 3000 | 12030.295
1700 | 60 | 580 | 640 |  |  | 5000 | 10484.1624
1800 | 60 | 600 | 660 |  |  | 6000 | 9982.2899
1900 | 70 | 640 | 710 |  |  | 7000 | 9576.9667
2000 | 70 | 680 | 750 |  |  | 8000 | 9239.3348
2100 | 70 | 720 | 790 |  |  | 9000 | 8951.5188
2200 | 80 | 760 | 840 |  |  | 10000 | 8701.7305
2300 | 80 | 770 | 850 |  |  | 20000 | 7225.0136
2400 | 90 | 810 | 900 |  |  | 40000 | 6001.0824
2500 | 90 | 850 | 940 |  |  | 50000 | 5653.4377
[6 empty] | 60000 | 5384.5442
[6 empty] | 70000 | 5167.2937
[6 empty] | 80000 | 4986.2759
[6 empty] | 90000 | 4831.929
[6 empty] | 100000 | 4697.9511

## Pipeline Pricing
Option 5B Pipeline Pricing
Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Pipe Wall thickness (mm) | Steel Mass (kg) | Pipe Area (m2) | Coating Cost | Delivery Cost | Pipe Cost | Chamber Cost R/m | Chamber Cost R | Pumpstation Name | Pump Station Power | Reservoir Name | Volume m3
2 | 1069.018 | 0 | 1.9 | 11.875 | 0 | 0 | 0 | 0 | 0 | 710 | 0 | PS1 | 2342 | BPT 3 | 35277.12
4 | 1067.321 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000 | PS3 | 12177 | BPT 5 | 35277.12
6 | 1064.035 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000 |  |  | BPT 2 | 35277.12
8 | 1063.832 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
10 | 1067.893 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
12 | 1075.133 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
14 | 1082.768 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
16 | 1089.726 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
18 | 1094.131 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
20 | 1097.897 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
22 | 1101.67 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
24 | 1095.952 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
26 | 1090.107 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
28 | 1085.781 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
30 | 1081.89 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
32 | 1077.937 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
34 | 1074.89 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
36 | 1071.114 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
38 | 1065.311 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
40 | 1059.051 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
42 | 1054.28 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
44 | 1053.871 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
46 | 1050.42 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
48 | 1052.704 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
50 | 1056.355 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
52 | 1058.466 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
54 | 1055.99 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
56 | 1055.66 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
58 | 1056.404 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
60 | 1056.841 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
62 | 1056.377 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
64 | 1052.503 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
66 | 1046.022 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
68 | 1036.575 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
70 | 1031.818 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
72 | 1027.675 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
74 | 1023.844 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
76 | 1020.888 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
78 | 1023.648 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
80 | 1027.566 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
82 | 1032.371 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
84 | 1034.983 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
86 | 1033.213 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
88 | 1031.188 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
90 | 1029.08 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
92 | 1026.322 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
94 | 1023.207 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
96 | 1021.503 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
98 | 1019.765 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
100 | 1018.493 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
102 | 1016.444 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
104 | 1013.288 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
106 | 1007.843 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
108 | 1001.282 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
110 | 996.609 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
112 | 992.999 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
114 | 993.639 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
116 | 994.611 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
118 | 995.751 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
120 | 996.479 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
122 | 996.147 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
124 | 992.094 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
126 | 985.623 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
128 | 977.759 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
130 | 969.772 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
132 | 981.785 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
134 | 991.458 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
136 | 987.77 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
138 | 982.725 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
140 | 977.559 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
142 | 975.289 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
144 | 973.968 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
146 | 962.473 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
148 | 951.285 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
150 | 948.174 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
152 | 944.641 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
154 | 941.566 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
156 | 940.942 | 2 | 1.9 | 11.875 | 1105894.9783 | 11938.0521 | 2387610.4167 | 170000 | 19353162.121 | 710 | 1420000
158 | 939.726 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
160 | 936.738 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
162 | 933.65 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
164 | 932.745 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
166 | 931.696 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
168 | 930.999 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
170 | 930.885 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
172 | 930.378 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
174 | 931.324 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
176 | 933.53 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
178 | 932.714 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
180 | 928.311 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
182 | 924.179 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
184 | 928.398 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
186 | 930.866 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
188 | 928.411 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
190 | 927.849 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
192 | 926.71 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
194 | 926.201 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
196 | 924.509 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
198 | 923.417 | 2 | 1.8 | 11.2952 | 996509.3057 | 11309.7336 | 2261946.7106 | 170000 | 17438912.8492 | 660 | 1320000
200 | 923.011 | 2 | 1.8 | 11.3195 | 998644.849 | 11309.7336 | 2261946.7106 | 170000 | 17476284.8575 | 660 | 1320000
202 | 921.969 | 2 | 1.8 | 11.3821 | 1004125.4583 | 11309.7336 | 2261946.7106 | 170000 | 17572195.5205 | 660 | 1320000
204 | 920.661 | 2 | 1.8 | 11.4605 | 1011004.6025 | 11309.7336 | 2261946.7106 | 170000 | 17692580.5441 | 660 | 1320000
206 | 920.243 | 2 | 1.8 | 11.4856 | 1013202.8554 | 11309.7336 | 2261946.7106 | 170000 | 17731049.9688 | 660 | 1320000
208 | 919.297 | 2 | 1.8 | 11.5424 | 1018177.6195 | 11309.7336 | 2261946.7106 | 170000 | 17818108.3416 | 660 | 1320000
210 | 917.533 | 2 | 1.8 | 11.6482 | 1027453.1808 | 11309.7336 | 2261946.7106 | 170000 | 17980430.6641 | 660 | 1320000
212 | 917.684 | 2 | 1.8 | 11.6392 | 1026659.2276 | 11309.7336 | 2261946.7106 | 170000 | 17966536.4829 | 660 | 1320000
214 | 915.724 | 2 | 1.8 | 11.7568 | 1036964.2159 | 11309.7336 | 2261946.7106 | 170000 | 18146873.7777 | 660 | 1320000
216 | 915.73 | 2 | 1.8 | 11.7564 | 1036932.6721 | 11309.7336 | 2261946.7106 | 170000 | 18146321.7612 | 660 | 1320000
218 | 915.584 | 2 | 1.8 | 11.7652 | 1037700.2343 | 11309.7336 | 2261946.7106 | 170000 | 18159754.0995 | 660 | 1320000
220 | 915.444 | 2 | 1.8 | 11.7736 | 1038436.2457 | 11309.7336 | 2261946.7106 | 170000 | 18172634.2995 | 660 | 1320000
222 | 913.52 | 2 | 1.8 | 11.889 | 1048550.4405 | 11309.7336 | 2261946.7106 | 170000 | 18349632.708 | 660 | 1320000
224 | 912.524 | 2 | 1.8 | 11.9488 | 1053785.7546 | 11309.7336 | 2261946.7106 | 170000 | 18441250.7056 | 660 | 1320000
226 | 912.565 | 2 | 1.8 | 11.9463 | 1053570.2516 | 11309.7336 | 2261946.7106 | 170000 | 18437479.4037 | 660 | 1320000
228 | 913.484 | 2 | 2.2 | 19.8 | 2129173.4923 | 13823.0077 | 2764601.5352 | 170000 | 37260536.1153 | 840 | 1680000
230 | 913.545 | 2 | 2.2 | 19.7558 | 2124467.1056 | 13823.0077 | 2764601.5352 | 170000 | 37178174.3479 | 840 | 1680000
232 | 914.546 | 2 | 2.2 | 19.6427 | 2112414.3333 | 13823.0077 | 2764601.5352 | 170000 | 36967250.8331 | 840 | 1680000
234 | 918.285 | 2 | 2.2 | 19.3288 | 2078957.6466 | 13823.0077 | 2764601.5352 | 170000 | 36381758.8156 | 840 | 1680000
236 | 919.357 | 2 | 2.2 | 19.2105 | 2066345.0001 | 13823.0077 | 2764601.5352 | 170000 | 36161037.5019 | 840 | 1680000
238 | 918.649 | 2 | 2.2 | 19.2228 | 2067648.5413 | 13823.0077 | 2764601.5352 | 170000 | 36183849.4721 | 840 | 1680000
240 | 922.974 | 2 | 2.2 | 18.8659 | 2029595.8547 | 13823.0077 | 2764601.5352 | 170000 | 35517927.4565 | 840 | 1680000
242 | 927.375 | 2 | 2.2 | 18.5035 | 1990936.0143 | 13823.0077 | 2764601.5352 | 170000 | 34841380.2499 | 840 | 1680000
244 | 929.253 | 2 | 2.2 | 18.3261 | 1972007.0597 | 13823.0077 | 2764601.5352 | 170000 | 34510123.5451 | 840 | 1680000
246 | 930.863 | 2 | 2.2 | 18.1683 | 1955172.3912 | 13823.0077 | 2764601.5352 | 170000 | 34215516.8455 | 840 | 1680000
248 | 931.924 | 2 | 2.2 | 18.0508 | 1942632.2961 | 13823.0077 | 2764601.5352 | 170000 | 33996065.1813 | 840 | 1680000
250 | 936.722 | 2 | 2.2 | 17.6593 | 1900834.9656 | 13823.0077 | 2764601.5352 | 170000 | 33264611.898 | 840 | 1680000
252 | 941.777 | 2 | 2.2 | 17.2489 | 1857009.5342 | 13823.0077 | 2764601.5352 | 170000 | 32497666.8489 | 840 | 1680000
254 | 948.143 | 2 | 2.2 | 16.7423 | 1802894.5158 | 13823.0077 | 2764601.5352 | 170000 | 31550654.026 | 840 | 1680000
256 | 955.417 | 2 | 2.2 | 16.1692 | 1741635.2535 | 13823.0077 | 2764601.5352 | 170000 | 30478616.937 | 840 | 1680000
258 | 962.7 | 2 | 2.2 | 15.5954 | 1680272.9878 | 13823.0077 | 2764601.5352 | 170000 | 29404777.286 | 840 | 1680000
260 | 969.281 | 2 | 2.2 | 15.0731 | 1624387.9565 | 13823.0077 | 2764601.5352 | 170000 | 28426789.2395 | 840 | 1680000
262 | 980.284 | 2 | 2.2 | 14.2265 | 1533748.4729 | 13823.0077 | 2764601.5352 | 170000 | 26840598.2756 | 840 | 1680000
264 | 986.551 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
266 | 989.198 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
268 | 994.39 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
270 | 999.917 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
272 | 1004.623 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
274 | 1008.819 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
276 | 1007.834 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
278 | 1005.626 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
280 | 1001.623 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
282 | 1004.052 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
284 | 1010.797 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
286 | 1014.67 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
288 | 1017.319 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
290 | 1027.459 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
292 | 1031.99 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
294 | 1036.254 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
296 | 1040.127 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
298 | 1044.396 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
300 | 1051.339 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
302 | 1060.955 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
304 | 1070.227 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
306 | 1072.691 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
308 | 1076.503 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
310 | 1083.996 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
312 | 1097.188 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
314 | 1103.545 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
316 | 1105.174 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
318 | 1111.657 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
320 | 1122.935 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
322 | 1128.197 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
324 | 1132.561 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
326 | 1131.854 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
328 | 1133.338 | 2 | 2.2 | 13.75 | 1482695.7604 | 13823.0077 | 2764601.5352 | 170000 | 25947175.8077 | 840 | 1680000
330 | 1136.405 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
332 | 1128.709 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
334 | 1120.713 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
336 | 1115.226 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
338 | 1108.709 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
340 | 1102.499 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
342 | 1096.349 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
344 | 1090.39 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
346 | 1087.765 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
348 | 1084.661 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
350 | 1081.662 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
352 | 1076.872 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
354 | 1070.898 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
356 | 1065.018 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
358 | 1059.58 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
360 | 1055.284 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
362 | 1050.886 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
364 | 1052.647 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
366 | 1051.117 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
368 | 1048.266 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
370 | 1040.172 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
372 | 1033.483 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
374 | 1030.95 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
376 | 1032.263 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
378 | 1031.391 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
380 | 1025.791 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
382 | 1020.911 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
384 | 1015.65 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
386 | 1012.139 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
388 | 1010.472 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
390 | 1005.401 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
392 | 996.666 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
394 | 991.35 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
396 | 990.486 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
398 | 992.761 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
400 | 999.077 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
402 | 1001.8 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
404 | 1002.224 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
406 | 1002.003 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
408 | 1003.596 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
410 | 994.111 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
412 | 983.925 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
414 | 972.347 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
416 | 963.901 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
418 | 963.258 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
420 | 965.872 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
422 | 966.177 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
424 | 973.825 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
426 | 983.972 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
428 | 994.096 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
430 | 991.695 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
432 | 984.933 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
434 | 974.509 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
436 | 966.698 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
438 | 963.618 | 2 | 1.8 | 11.25 | 992548.4016 | 11309.7336 | 2261946.7106 | 170000 | 17369597.0283 | 660 | 1320000
440 | 957.803 | 2 | 1.8 | 11.3161 | 998345.0349 | 11309.7336 | 2261946.7106 | 170000 | 17471038.1102 | 660 | 1320000
442 | 954.277 | 2 | 1.8 | 11.5277 | 1016889.2597 | 11309.7336 | 2261946.7106 | 170000 | 17795562.0451 | 660 | 1320000
444 | 947.182 | 2 | 1.8 | 11.9534 | 1054190.4781 | 11309.7336 | 2261946.7106 | 170000 | 18448333.3664 | 660 | 1320000
446 | 938.045 | 2 | 1.8 | 12.5016 | 1102200.9626 | 11309.7336 | 2261946.7106 | 170000 | 19288516.8457 | 660 | 1320000
448 | 930.871 | 2 | 1.8 | 12.932 | 1139876.0607 | 11309.7336 | 2261946.7106 | 170000 | 19947831.0631 | 660 | 1320000
450 | 926.391 | 2 | 1.8 | 13.2008 | 1163394.033 | 11309.7336 | 2261946.7106 | 170000 | 20359395.5772 | 660 | 1320000
452 | 918.344 | 2 | 1.8 | 13.6837 | 1205619.2415 | 11309.7336 | 2261946.7106 | 170000 | 21098336.7266 | 660 | 1320000
454 | 911.505 | 2 | 1.8 | 14.094 | 1241487.607 | 11309.7336 | 2261946.7106 | 170000 | 21726033.1221 | 660 | 1320000
456 | 903.61 | 2 | 1.8 | 14.5677 | 1282873.6994 | 11309.7336 | 2261946.7106 | 170000 | 22450289.7388 | 660 | 1320000
458 | 900.63 | 2 | 1.8 | 14.7465 | 1298489.2946 | 11309.7336 | 2261946.7106 | 170000 | 22723562.6559 | 660 | 1320000
460 | 904.066 | 2 | 1.8 | 14.5403 | 1280483.9207 | 11309.7336 | 2261946.7106 | 170000 | 22408468.6118 | 660 | 1320000
462 | 915.092 | 2 | 1.8 | 13.8788 | 1222677.0116 | 11309.7336 | 2261946.7106 | 170000 | 21396847.7035 | 660 | 1320000
464 | 905.556 | 2 | 1.8 | 14.4509 | 1272674.6991 | 11309.7336 | 2261946.7106 | 170000 | 22271807.2348 | 660 | 1320000
466 | 905.271 | 2 | 1.8 | 14.468 | 1274168.4703 | 11309.7336 | 2261946.7106 | 170000 | 22297948.2298 | 660 | 1320000
468 | 901.918 | 2 | 1.8 | 14.6692 | 1291740.3907 | 11309.7336 | 2261946.7106 | 170000 | 22605456.8381 | 660 | 1320000
470 | 895.651 | 2 | 1.8 | 15.0452 | 1324572.8786 | 11309.7336 | 2261946.7106 | 170000 | 23180025.3754 | 660 | 1320000
472 | 892.304 | 2 | 1.8 | 15.2461 | 1342101.9243 | 11309.7336 | 2261946.7106 | 170000 | 23486783.6755 | 660 | 1320000
474 | 895.279 | 2 | 1.8 | 15.0676 | 1326521.3288 | 11309.7336 | 2261946.7106 | 170000 | 23214123.2534 | 660 | 1320000
476 | 896.818 | 2 | 1.8 | 14.9752 | 1318460.0829 | 11309.7336 | 2261946.7106 | 170000 | 23073051.4515 | 660 | 1320000
478 | 909.921 | 2 | 1.8 | 14.189 | 1249792.8108 | 11309.7336 | 2261946.7106 | 170000 | 21871374.189 | 660 | 1320000
480 | 926.295 | 2 | 1.8 | 13.2066 | 1163897.9115 | 11309.7336 | 2261946.7106 | 170000 | 20368213.4517 | 660 | 1320000
482 | 924.888 | 2 | 1.5 | 11.0758 | 813390.6291 | 9424.778 | 1884955.5922 | 170000 | 14234336.0099 | 580 | 1160000
484 | 919.044 | 2 | 1.5 | 11.368 | 834685.4365 | 9424.778 | 1884955.5922 | 170000 | 14606995.139 | 580 | 1160000
486 | 911.164 | 2 | 1.5 | 11.7621 | 863385.8389 | 9424.778 | 1884955.5922 | 170000 | 15109252.1813 | 580 | 1160000
488 | 903.893 | 2 | 1.5 | 12.1256 | 889854.568 | 9424.778 | 1884955.5922 | 170000 | 15572454.9393 | 580 | 1160000
490 | 901.953 | 2 | 1.5 | 12.2226 | 896914.5753 | 9424.778 | 1884955.5922 | 170000 | 15696005.0674 | 580 | 1160000
492 | 900.198 | 2 | 1.5 | 12.3103 | 903300.5349 | 9424.778 | 1884955.5922 | 170000 | 15807759.3601 | 580 | 1160000
494 | 904.177 | 2 | 1.5 | 12.1114 | 888820.9632 | 9424.778 | 1884955.5922 | 170000 | 15554366.8565 | 580 | 1160000
496 | 912.253 | 2 | 1.5 | 11.7076 | 859420.4135 | 9424.778 | 1884955.5922 | 170000 | 15039857.2362 | 580 | 1160000
498 | 915.297 | 2 | 1.5 | 11.5554 | 848334.606 | 9424.778 | 1884955.5922 | 170000 | 14845855.6046 | 580 | 1160000
500 | 919.629 | 2 | 1.5 | 9.375 | 689269.7233 | 9424.778 | 1884955.5922 | 170000 | 12062220.1585 | 580 | 1160000

## Pipeline Instalation Costs
Option 7 Excavation and Back Fill Pricing
Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Trench Width (m) | Trench Depth (m) | Excavation (m3) | Bedding and Cradle Fill (m3) | Main fill (m3) | Spoil (m3) | Excavation Cost | Bedding and Cradle Fill Cost | Main Fill Cost | Spoil Cost
2 | 1069.018 | 0 | 1.9 | 2.9 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1067.321 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
6 | 1064.035 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
8 | 1063.832 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
10 | 1067.893 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
12 | 1075.133 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
14 | 1082.768 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
16 | 1089.726 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
18 | 1094.131 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
20 | 1097.897 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
22 | 1101.67 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
24 | 1095.952 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
26 | 1090.107 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
28 | 1085.781 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
30 | 1081.89 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
32 | 1077.937 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
34 | 1074.89 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
36 | 1071.114 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
38 | 1065.311 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
40 | 1059.051 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
42 | 1054.28 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
44 | 1053.871 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
46 | 1050.42 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
48 | 1052.704 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
50 | 1056.355 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
52 | 1058.466 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
54 | 1055.99 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
56 | 1055.66 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
58 | 1056.404 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
60 | 1056.841 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
62 | 1056.377 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
64 | 1052.503 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
66 | 1046.022 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
68 | 1036.575 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
70 | 1031.818 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
72 | 1027.675 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
74 | 1023.844 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
76 | 1020.888 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
78 | 1023.648 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
80 | 1027.566 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
82 | 1032.371 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
84 | 1034.983 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
86 | 1033.213 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
88 | 1031.188 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
90 | 1029.08 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
92 | 1026.322 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
94 | 1023.207 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
96 | 1021.503 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
98 | 1019.765 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
100 | 1018.493 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
102 | 1016.444 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
104 | 1013.288 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
106 | 1007.843 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
108 | 1001.282 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
110 | 996.609 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
112 | 992.999 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
114 | 993.639 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
116 | 994.611 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
118 | 995.751 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
120 | 996.479 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
122 | 996.147 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
124 | 992.094 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
126 | 985.623 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
128 | 977.759 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
130 | 969.772 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
132 | 981.785 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
134 | 991.458 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
136 | 987.77 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
138 | 982.725 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
140 | 977.559 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
142 | 975.289 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
144 | 973.968 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
146 | 962.473 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
148 | 951.285 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
150 | 948.174 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
152 | 944.641 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
154 | 941.566 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
156 | 940.942 | 2 | 1.9 | 2.9 | 3.9 | 22620 | 8249.4253 | 8700 | 5670.5747 | 1131000 | 1361155.1679 | 478500 | 255175.8633
158 | 939.726 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
160 | 936.738 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
162 | 933.65 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
164 | 932.745 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
166 | 931.696 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
168 | 930.999 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
170 | 930.885 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
172 | 930.378 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
174 | 931.324 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
176 | 933.53 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
178 | 932.714 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
180 | 928.311 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
182 | 924.179 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
184 | 928.398 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
186 | 930.866 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
188 | 928.411 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
190 | 927.849 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
192 | 926.71 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
194 | 926.201 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
196 | 924.509 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
198 | 923.417 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
200 | 923.011 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
202 | 921.969 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
204 | 920.661 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
206 | 920.243 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
208 | 919.297 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
210 | 917.533 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
212 | 917.684 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
214 | 915.724 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
216 | 915.73 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
218 | 915.584 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
220 | 915.444 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
222 | 913.52 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
224 | 912.524 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
226 | 912.565 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
228 | 913.484 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
230 | 913.545 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
232 | 914.546 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
234 | 918.285 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
236 | 919.357 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
238 | 918.649 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
240 | 922.974 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
242 | 927.375 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
244 | 929.253 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
246 | 930.863 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
248 | 931.924 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
250 | 936.722 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
252 | 941.777 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
254 | 948.143 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
256 | 955.417 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
258 | 962.7 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
260 | 969.281 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
262 | 980.284 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
264 | 986.551 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
266 | 989.198 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
268 | 994.39 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
270 | 999.917 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
272 | 1004.623 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
274 | 1008.819 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
276 | 1007.834 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
278 | 1005.626 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
280 | 1001.623 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
282 | 1004.052 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
284 | 1010.797 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
286 | 1014.67 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
288 | 1017.319 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
290 | 1027.459 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
292 | 1031.99 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
294 | 1036.254 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
296 | 1040.127 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
298 | 1044.396 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
300 | 1051.339 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
302 | 1060.955 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
304 | 1070.227 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
306 | 1072.691 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
308 | 1076.503 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
310 | 1083.996 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
312 | 1097.188 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
314 | 1103.545 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
316 | 1105.174 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
318 | 1111.657 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
320 | 1122.935 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
322 | 1128.197 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
324 | 1132.561 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
326 | 1131.854 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
328 | 1133.338 | 2 | 2.2 | 3.2 | 4.2 | 26880 | 9677.3458 | 9600 | 7602.6542 | 1344000 | 1596762.0534 | 528000 | 342119.44
330 | 1136.405 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
332 | 1128.709 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
334 | 1120.713 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
336 | 1115.226 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
338 | 1108.709 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
340 | 1102.499 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
342 | 1096.349 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
344 | 1090.39 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
346 | 1087.765 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
348 | 1084.661 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
350 | 1081.662 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
352 | 1076.872 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
354 | 1070.898 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
356 | 1065.018 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
358 | 1059.58 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
360 | 1055.284 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
362 | 1050.886 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
364 | 1052.647 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
366 | 1051.117 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
368 | 1048.266 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
370 | 1040.172 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
372 | 1033.483 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
374 | 1030.95 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
376 | 1032.263 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
378 | 1031.391 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
380 | 1025.791 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
382 | 1020.911 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
384 | 1015.65 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
386 | 1012.139 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
388 | 1010.472 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
390 | 1005.401 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
392 | 996.666 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
394 | 991.35 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
396 | 990.486 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
398 | 992.761 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
400 | 999.077 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
402 | 1001.8 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
404 | 1002.224 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
406 | 1002.003 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
408 | 1003.596 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
410 | 994.111 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
412 | 983.925 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
414 | 972.347 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
416 | 963.901 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
418 | 963.258 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
420 | 965.872 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
422 | 966.177 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
424 | 973.825 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
426 | 983.972 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
428 | 994.096 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
430 | 991.695 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
432 | 984.933 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
434 | 974.509 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
436 | 966.698 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
438 | 963.618 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
440 | 957.803 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
442 | 954.277 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
444 | 947.182 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
446 | 938.045 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
448 | 930.871 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
450 | 926.391 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
452 | 918.344 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
454 | 911.505 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
456 | 903.61 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
458 | 900.63 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
460 | 904.066 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
462 | 915.092 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
464 | 905.556 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
466 | 905.271 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
468 | 901.918 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
470 | 895.651 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
472 | 892.304 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
474 | 895.279 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
476 | 896.818 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
478 | 909.921 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
480 | 926.295 | 2 | 1.8 | 2.8 | 3.8 | 21280 | 7790.6199 | 8400 | 5089.3801 | 1064000 | 1285452.2837 | 462000 | 229022.1044
482 | 924.888 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
484 | 919.044 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
486 | 911.164 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
488 | 903.893 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
490 | 901.953 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
492 | 900.198 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
494 | 904.177 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
496 | 912.253 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
498 | 915.297 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281
500 | 919.629 | 2 | 1.5 | 2.5 | 3.5 | 17500 | 6465.7083 | 7500 | 3534.2917 | 875000 | 1066841.8637 | 412500 | 159043.1281

## Capital Costs
Option 5B Capital Costs
Pipe Cost | 5757485865.9443
Pipe Laying and Joining | 1151497173.1889
Pipe Trench Excavation & Back Fill | 805370452.5696
Air Valve, Scour Valve & Isolating Cost | 353140000
Pump Station Cost PS 1 | 31430340.9711
Pump Station Cost PS 3 | 105960972.005
Reservoir Cost BPT 3 | 2822169.6
Reservoir Cost BPT 5 | 2822169.6
Reservoir Cost BPT 2 | 2822169.6
Option 5B Capital Costs (Pula)
Pipe Cost | 5234078059.9494
Pipe Laying and Joining | 1046815611.9899
Pipe Trench Excavation & Back Fill | 732154956.8815
Air Valve, Scour Valve & Isolating Cost | 321036363.6364
Pump Station Cost PS 1 | 28573037.2465
Pump Station Cost PS 3 | 96328156.3682
Reservoir Cost BPT 3 | 2565608.7273
Reservoir Cost BPT 5 | 2565608.7273
Reservoir Cost BPT 2 | 2565608.7273

## Maintenance Costs
Option 5B Maintenance Costs
Item | Percentage Per Annum | Cost R/year
Civil | 0.5% | 28829761.8737
Mechanical & Electrical | 4% | 19621252.519
Total |  | 48451014.3928
Option 5B Maintenance Costs (Pula)
Item | Percentage Per Annum | Cost P/year
Civil | 0.5% | 26208874.4307
Mechanical & Electrical | 4% | 17837502.29
Total |  | 44046376.7207

## Pumping Costs Calculation
Option 5B Pumping Costs Calculations - PS 1
Pipeline Details |  |  |  | New Pipe Flow Equation |  |  | Average Pipe Flow Equation |  |  | Old Pipe Flow Equation |  |  | Biofilm Pipe Flow Equation
Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component
2 | 1069.018 | 0 | 1.9 | 0.00867 | 0 | 0 | 0.0097304 | 0 | 0 | 0.011459 | 0 | 0 | 0.014543 | 0 | 0
4 | 1067.321 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042 | 1.618 | 0.063419
6 | 1064.035 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042 | 1.618 | 0.063419
8 | 1063.832 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042 | 1.618 | 0.063419
10 | 1067.893 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042 | 1.618 | 0.063419
12 | 1075.133 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042 | 1.618 | 0.063419
14 | 1082.768 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042 | 1.618 | 0.063419
16 | 1089.726 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042 | 1.618 | 0.063419
18 | 1094.131 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042 | 1.618 | 0.063419
20 | 1097.897 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042 | 1.618 | 0.063419
22 | 1101.67 | 2 | 1.9 | 0.00867 | 0.057863 | 0.0038042 | 0.0097304 | 0.06494 | 0.0038042 | 0.011459 | 0.076477 | 0.0038042 | 0.014543 | 0.097058 | 0.0038042 | 1.618 | 0.063419
16.8147
Option 5B Pumping Costs Calculations - PS 3
Pipeline Details |  |  |  | New Pipe Flow Equation |  |  | Average Pipe Flow Equation |  |  | Old Pipe Flow Equation |  |  | Biofilm Pipe Flow Equation
Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component | λ | Friction Component | Secondary Loss Component
228 | 913.484 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
230 | 913.545 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
232 | 914.546 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
234 | 918.285 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
236 | 919.357 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
238 | 918.649 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
240 | 922.974 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
242 | 927.375 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
244 | 929.253 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
246 | 930.863 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
248 | 931.924 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
250 | 936.722 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
252 | 941.777 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
254 | 948.143 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
256 | 955.417 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
258 | 962.7 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
260 | 969.281 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
262 | 980.284 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
264 | 986.551 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
266 | 989.198 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
268 | 994.39 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
270 | 999.917 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
272 | 1004.623 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
274 | 1008.819 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
276 | 1007.834 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
278 | 1005.626 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
280 | 1001.623 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
282 | 1004.052 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
284 | 1010.797 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
286 | 1014.67 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
288 | 1017.319 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
290 | 1027.459 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
292 | 1031.99 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
294 | 1036.254 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
296 | 1040.127 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
298 | 1044.396 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
300 | 1051.339 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
302 | 1060.955 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
304 | 1070.227 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
306 | 1072.691 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
308 | 1076.503 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
310 | 1083.996 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
312 | 1097.188 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
314 | 1103.545 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
316 | 1105.174 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
318 | 1111.657 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
320 | 1122.935 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
322 | 1128.197 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
324 | 1132.561 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
326 | 1131.854 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
328 | 1133.338 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
330 | 1136.405 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
332 | 1128.709 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
334 | 1120.713 | 2 | 2.2 | 0.008468 | 0.027153 | 0.0021163 | 0.0094904 | 0.030432 | 0.0021163 | 0.011153 | 0.035762 | 0.0021163 | 0.014105 | 0.045227 | 0.0021163
336 | 1115.226 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
338 | 1108.709 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
340 | 1102.499 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
342 | 1096.349 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
344 | 1090.39 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
346 | 1087.765 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
348 | 1084.661 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
350 | 1081.662 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
352 | 1076.872 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
354 | 1070.898 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
356 | 1065.018 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
358 | 1059.58 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
360 | 1055.284 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
362 | 1050.886 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
364 | 1052.647 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
366 | 1051.117 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
368 | 1048.266 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
370 | 1040.172 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
372 | 1033.483 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
374 | 1030.95 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
376 | 1032.263 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
378 | 1031.391 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
380 | 1025.791 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
382 | 1020.911 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
384 | 1015.65 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
386 | 1012.139 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
388 | 1010.472 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
390 | 1005.401 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
392 | 996.666 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
394 | 991.35 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
396 | 990.486 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
398 | 992.761 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
400 | 999.077 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
402 | 1001.8 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
404 | 1002.224 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
406 | 1002.003 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
408 | 1003.596 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
410 | 994.111 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
412 | 983.925 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
414 | 972.347 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
416 | 963.901 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
418 | 963.258 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
420 | 965.836 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
422 | 966.309 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
424 | 972.884 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
426 | 983.972 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
428 | 994.096 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
430 | 991.695 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
432 | 984.933 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
434 | 978.185 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
436 | 972.686 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
438 | 966.824 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
440 | 960.902 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
442 | 952.924 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
444 | 945.683 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
446 | 941.042 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
448 | 937.104 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
450 | 939.943 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
452 | 944.776 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
454 | 947.762 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
456 | 952.649 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
458 | 954.554 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
460 | 952.37 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
462 | 947.552 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
464 | 941.898 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
466 | 940.521 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
468 | 939.702 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
470 | 937.147 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
472 | 933.872 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
474 | 933.184 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
476 | 939.292 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
478 | 944.619 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
480 | 954.023 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
482 | 968.263 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
484 | 970.384 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
486 | 964.636 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
488 | 956.631 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
490 | 947.426 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
492 | 941.72 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
494 | 935.985 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
496 | 930.475 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
498 | 927.611 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
500 | 931.256 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
502 | 920.044 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
504 | 911.78 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
506 | 907.989 | 2 | 1.8 | 0.0087463 | 0.076492 | 0.0047226 | 0.0098211 | 0.085892 | 0.0047226 | 0.011575 | 0.10123 | 0.0047226 | 0.01471 | 0.12864 | 0.0047226
508 | 907.289 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
510 | 900.577 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
512 | 902.112 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
514 | 900.179 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
516 | 903.811 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
518 | 910.027 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928
520 | 911.131 | 2 | 1.5 | 0.0090113 | 0.1961 | 0.0097928 | 0.010137 | 0.2206 | 0.0097928 | 0.01198 | 0.2607 | 0.0097928 | 0.015294 | 0.33283 | 0.0097928

## Pumping Costs
Option 5B Pumping Costs
PS 1
New Pipe - Year 4 to 18 |  | Average Pipe - Year 19 to 33 |  | Old Pipe - Year 34 to 48 |  | Biofilmed Pipe - Year 49 to 63
Pumping Head (m) | 50 | Pumping Head (m) | 50 | Pumping Head (m) | 50 | Pumping Head (m) | 50
Gravitational Head (m) | -32.652 | Gravitational Head (m) | -32.652 | Gravitational Head (m) | -32.652 | Gravitational Head (m) | -32.652
Flow Rate (m3/s) | 5.3039 | Flow Rate (m3/s) | 5.0235 | Flow Rate (m3/s) | 4.6486 | Flow Rate (m3/s) | 4.1472
Pumping Hours per Day | 24 | Pumping Hours per Day | 24 | Pumping Hours per Day | 24 | Pumping Hours per Day | 24
Peak Design Flow (m3/s) | 4.083 | Peak Design Flow | 4.083 | Peak Design Flow | 4.083 | Peak Design Flow | 4.083
Required Pumping Hours | 18.5 | Required Pumping Hours | 19.5 | Required Pumping Hours | 21.1 | Required Pumping Hours | 23.6
Pumpstation Power (kW) | 2342 | Pumpstation Power (kW) | 2342 | Pumpstation Power (kW) | 2342 | Pumpstation Power (kW) | 2342
Pumping Days per Year | 347 | Pumping Days per Year | 347 | Pumping Days per Year | 347 | Pumping Days per Year | 347
Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699
Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388
Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056
Energy Cost Per Year | 6774274.7406 | Energy Cost Per Year | 7140433.1381 | Energy Cost Per Year | 7726286.574 | Energy Cost Per Year | 8641682.5676
Option 5B Pumping Costs
PS 3
New Pipe - Year 4 to 18 |  | Average Pipe - Year 19 to 33 |  | Old Pipe - Year 34 to 48 |  | Biofilmed Pipe - Year 49 to 63
Pumping Head (m) | 160 | Pumping Head (m) | 160 | Pumping Head (m) | 160 | Pumping Head (m) | 160
Gravitational Head (m) | 188.186 | Gravitational Head (m) | 188.186 | Gravitational Head (m) | 188.186 | Gravitational Head (m) | 188.186
Flow Rate (m3/s) | 5.8989 | Flow Rate (m3/s) | 5.5849 | Flow Rate (m3/s) | 5.1652 | Flow Rate (m3/s) | 4.6043
Pumping Hours per Day | 24 | Pumping Hours per Day | 24 | Pumping Hours per Day | 24 | Pumping Hours per Day | 24
Peak Design Flow (m3/s) | 4.083 | Peak Design Flow | 4.083 | Peak Design Flow | 4.083 | Peak Design Flow | 4.083
Required Pumping Hours | 16.6 | Required Pumping Hours | 17.5 | Required Pumping Hours | 19 | Required Pumping Hours | 21.3
Pumpstation Power (kW) | 12177 | Pumpstation Power (kW) | 12177 | Pumpstation Power (kW) | 12177 | Pumpstation Power (kW) | 12177
Pumping Days per Year | 347 | Pumping Days per Year | 347 | Pumping Days per Year | 347 | Pumping Days per Year | 347
Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699 | Fixed Power Cost per Month | 28.699
Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388 | Fixed power Cost per Year | 344.388
Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056 | Power Cost Per kWh | 0.45056
Energy Cost Per Year | 31603503.813 | Energy Cost Per Year | 33316928.1192 | Energy Cost Per Year | 36172635.2962 | Energy Cost Per Year | 40551386.3008
Pipe Type | Energy Cost Per Year PS 1 | Energy Cost Per Year PS 2
New Pipe | 6774274.7406 | 31603503.813
Average Pipe | 7140433.1381 | 33316928.1192
Old Pipe | 7726286.574 | 36172635.2962
Biofilm Pipe | 8641682.5676 | 40551386.3008
Pipe Type | Energy Cost Per Year PS 1 (Pula) | Energy Cost Per Year PS 2 (Pula)
New Pipe | 6158431.5824 | 28730458.0118
Average Pipe | 6491302.8528 | 30288116.472
Old Pipe | 7023896.8854 | 32884213.9056
Biofilm Pipe | 7856075.0614 | 36864896.6371

## Life Cycle Costing (Pula)
Table 38: Option 5B Life Cycle Costing (Pula)
Year | Reference Year | Capital Cost | Electricity - Pumping Cost | Maintenance Cost | NPV at 6% Discount Rate | NPV at 8% Discount Rate | NPV at 10% Discount Rate
2010 | 0 | 1866670753.0634 |  |  | 1866670753.0634 | 1866670753.0634 | 1866670753.0634
2011 | 1 | 1866670753.0634 |  |  | 1866670753.0634 | 1866670753.0634 | 1866670753.0634
2012 | 2 | 1866670753.0634 |  |  | 1866670753.0634 | 1866670753.0634 | 1866670753.0634
2013 | 3 | 1866670753.0634 |  |  | 1866670753.0634 | 1866670753.0634 | 1866670753.0634
2014 | 4 | 0 | 34888889.5942 | 44046376.7207 | 62524124.2541 | 58019777.1799 | 53913848.9959
2015 | 5 | 0 | 34888889.5942 | 44046376.7207 | 58985022.8812 | 53722015.9073 | 49012589.9963
2016 | 6 | 0 | 34888889.5942 | 44046376.7207 | 55646248.0011 | 49742607.3216 | 44556899.9966
2017 | 7 | 0 | 34888889.5942 | 44046376.7207 | 52496460.3784 | 46057969.7422 | 40506272.7242
2018 | 8 | 0 | 34888889.5942 | 44046376.7207 | 49524962.6212 | 42646268.2798 | 36823884.2947
2019 | 9 | 0 | 34888889.5942 | 44046376.7207 | 46721662.8501 | 39487285.4443 | 33476258.4498
2020 | 10 | 0 | 34888889.5942 | 44046376.7207 | 44077040.4247 | 36562301.3373 | 30432962.2271
2021 | 11 | 0 | 34888889.5942 | 44046376.7207 | 41582113.6082 | 33853982.7197 | 27666329.2973
2022 | 12 | 0 | 34888889.5942 | 44046376.7207 | 39228409.0643 | 31346280.296 | 25151208.4521
2023 | 13 | 0 | 34888889.5942 | 44046376.7207 | 37007933.0795 | 29024333.6075 | 22864734.9565
2024 | 14 | 0 | 34888889.5942 | 44046376.7207 | 34913144.4147 | 26874382.9699 | 20786122.6877
2025 | 15 | 0 | 34888889.5942 | 44046376.7207 | 32936928.6931 | 24883687.9351 | 18896475.1706
2026 | 16 | 0 | 34888889.5942 | 44046376.7207 | 31072574.2388 | 23040451.7917 | 17178613.7915
2027 | 17 | 0 | 34888889.5942 | 44046376.7207 | 29313749.2818 | 21333751.659 | 15616921.6286
2028 | 18 | 0 | 34888889.5942 | 44046376.7207 | 27654480.4546 | 19753473.7583 | 14197201.4806
2029 | 19 | 0 | 36779419.3248 | 44046376.7207 | 26713977.177 | 18728312.0259 | 13215663.5184
2030 | 20 | 0 | 36779419.3248 | 44046376.7207 | 25201865.2613 | 17341029.6536 | 12014239.5621
2031 | 21 | 0 | 36779419.3248 | 44046376.7207 | 23775344.5861 | 16056508.9385 | 10922035.9656
2032 | 22 | 0 | 36779419.3248 | 44046376.7207 | 22429570.3643 | 14867137.906 | 9929123.6051
2033 | 23 | 0 | 36779419.3248 | 44046376.7207 | 21159972.0418 | 13765868.4315 | 9026476.0046
2034 | 24 | 0 | 36779419.3248 | 44046376.7207 | 19962237.7753 | 12746174.4736 | 8205887.2769
2035 | 25 | 0 | 36779419.3248 | 44046376.7207 | 18832299.788 | 11802013.4015 | 7459897.5245
2036 | 26 | 0 | 36779419.3248 | 44046376.7207 | 17766320.5547 | 10927790.1866 | 6781725.0223
2037 | 27 | 0 | 36779419.3248 | 44046376.7207 | 16760679.7686 | 10118324.2468 | 6165204.5657
2038 | 28 | 0 | 36779419.3248 | 44046376.7207 | 15811962.0458 | 9368818.747 | 5604731.4233
2039 | 29 | 0 | 36779419.3248 | 44046376.7207 | 14916945.3263 | 8674832.1732 | 5095210.3849
2040 | 30 | 0 | 36779419.3248 | 44046376.7207 | 14072589.9304 | 8032252.0122 | 4632009.4408
2041 | 31 | 0 | 36779419.3248 | 44046376.7207 | 13276028.2363 | 7437270.3817 | 4210917.6734
2042 | 32 | 0 | 36779419.3248 | 44046376.7207 | 12524554.9399 | 6886361.4645 | 3828106.9759
2043 | 33 | 0 | 36779419.3248 | 44046376.7207 | 11815617.8678 | 6376260.6153 | 3480097.2508
2044 | 34 | 0 | 39908110.791 | 44046376.7207 | 11578291.9406 | 6132481.2401 | 3286189.6199
2045 | 35 | 0 | 39908110.791 | 44046376.7207 | 10922916.9251 | 5678223.3704 | 2987445.109
2046 | 36 | 0 | 39908110.791 | 44046376.7207 | 10304638.6086 | 5257614.2319 | 2715859.19
2047 | 37 | 0 | 39908110.791 | 44046376.7207 | 9721357.1779 | 4868161.3258 | 2468962.9
2048 | 38 | 0 | 39908110.791 | 44046376.7207 | 9171091.6773 | 4507556.7832 | 2244511.7272
2049 | 39 | 0 | 39908110.791 | 44046376.7207 | 8651973.2805 | 4173663.6881 | 2040465.2066
2050 | 40 | 0 | 39908110.791 | 44046376.7207 | 8162238.9438 | 3864503.4149 | 1854968.3696
2051 | 41 | 0 | 39908110.791 | 44046376.7207 | 7700225.4187 | 3578243.9027 | 1686334.8815
2052 | 42 | 0 | 39908110.791 | 44046376.7207 | 7264363.6026 | 3313188.7988 | 1533031.7104
2053 | 43 | 0 | 39908110.791 | 44046376.7207 | 6853173.21 | 3067767.4063 | 1393665.1913
2054 | 44 | 0 | 39908110.791 | 44046376.7207 | 6465257.7452 | 2840525.3762 | 1266968.3557
2055 | 45 | 0 | 39908110.791 | 44046376.7207 | 6099299.7597 | 2630116.0891 | 1151789.4143
2056 | 46 | 0 | 39908110.791 | 44046376.7207 | 5754056.377 | 2435292.6751 | 1047081.2857
2057 | 47 | 0 | 39908110.791 | 44046376.7207 | 5428355.0727 | 2254900.6251 | 951892.0779
2058 | 48 | 0 | 39908110.791 | 44046376.7207 | 5121089.6912 | 2087870.9491 | 865356.4345
2059 | 49 | 0 | 44720971.6986 | 44046376.7207 | 5108175.9642 | 2044039.2378 | 831786.1304
2060 | 50 | 0 | 44720971.6986 | 44046376.7207 | 4819033.9285 | 1892628.9239 | 756169.2095
2061 | 51 | 0 | 44720971.6986 | 44046376.7207 | 4546258.4231 | 1752434.1888 | 687426.554
2062 | 52 | 0 | 44720971.6986 | 44046376.7207 | 4288923.0407 | 1622624.2489 | 624933.231
2063 | 53 | 0 | 44720971.6986 | 44046376.7207 | 4046153.8119 | 1502429.8601 | 568121.119
2064 | 54 | 0 | 44720971.6986 | 44046376.7207 | 3817126.2377 | 1391138.7593 | 516473.7446
2065 | 55 | 0 | 44720971.6986 | 44046376.7207 | 3601062.4884 | 1288091.4438 | 469521.586
2066 | 56 | 0 | 44720971.6986 | 44046376.7207 | 3397228.7626 | 1192677.2628 | 426837.8054
2067 | 57 | 0 | 44720971.6986 | 44046376.7207 | 3204932.7949 | 1104330.7989 | 388034.3686
2068 | 58 | 0 | 44720971.6986 | 44046376.7207 | 3023521.5047 | 1022528.5175 | 352758.5169
2069 | 59 | 0 | 44720971.6986 | 44046376.7207 | 2852378.778 | 946785.6643 | 320689.5608
2070 | 60 | 0 | 44720971.6986 | 44046376.7207 | 2690923.3754 | 876653.3929 | 291535.9644
2071 | 61 | 0 | 44720971.6986 | 44046376.7207 | 2538606.958 | 811716.1045 | 265032.6949
2072 | 62 | 0 | 44720971.6986 | 44046376.7207 | 2394912.2245 | 751588.9857 | 240938.8135
2073 | 63 | 0 | 44720971.6986 | 44046376.7207 | 2259351.1552 | 695915.7275 | 219035.285
[5 empty] | 8557174751.0417 | 8251746229.8544 | 8062788478.655

## Life Cycle Costing
Table 38: Option 5B Life Cycle Costing
Year | Reference Year | Capital Cost | Electricity - Pumping Cost | Maintenance Cost | NPV at 6% Discount Rate | NPV at 8% Discount Rate | NPV at 10% Discount Rate
2010 | 0 | 2053337828.3697 |  |  | 2053337828.3697 | 2053337828.3697 | 2053337828.3697
2011 | 1 | 2053337828.3697 |  |  | 2053337828.3697 | 2053337828.3697 | 2053337828.3697
2012 | 2 | 2053337828.3697 |  |  | 2053337828.3697 | 2053337828.3697 | 2053337828.3697
2013 | 3 | 2053337828.3697 |  |  | 2053337828.3697 | 2053337828.3697 | 2053337828.3697
2014 | 4 | 0 | 38377778.5537 | 48451014.3928 | 68776536.6795 | 63821754.8979 | 59305233.8955
2015 | 5 | 0 | 38377778.5537 | 48451014.3928 | 64883525.1693 | 59094217.4981 | 53913848.9959
2016 | 6 | 0 | 38377778.5537 | 48451014.3928 | 61210872.8012 | 54716868.0538 | 49012589.9963
2017 | 7 | 0 | 38377778.5537 | 48451014.3928 | 57746106.4163 | 50663766.7164 | 44556899.9966
2018 | 8 | 0 | 38377778.5537 | 48451014.3928 | 54477458.8833 | 46910895.1078 | 40506272.7242
2019 | 9 | 0 | 38377778.5537 | 48451014.3928 | 51393829.1352 | 43436013.9887 | 36823884.2947
2020 | 10 | 0 | 38377778.5537 | 48451014.3928 | 48484744.4671 | 40218531.471 | 33476258.4498
2021 | 11 | 0 | 38377778.5537 | 48451014.3928 | 45740324.969 | 37239380.9917 | 30432962.2271
2022 | 12 | 0 | 38377778.5537 | 48451014.3928 | 43151249.9707 | 34480908.3257 | 27666329.2973
2023 | 13 | 0 | 38377778.5537 | 48451014.3928 | 40708726.3875 | 31926766.9682 | 25151208.4521
2024 | 14 | 0 | 38377778.5537 | 48451014.3928 | 38404458.8561 | 29561821.2668 | 22864734.9565
2025 | 15 | 0 | 38377778.5537 | 48451014.3928 | 36230621.5624 | 27372056.7286 | 20786122.6877
2026 | 16 | 0 | 38377778.5537 | 48451014.3928 | 34179831.6626 | 25344496.9709 | 18896475.1706
2027 | 17 | 0 | 38377778.5537 | 48451014.3928 | 32245124.21 | 23467126.8249 | 17178613.7915
2028 | 18 | 0 | 38377778.5537 | 48451014.3928 | 30419928.5 | 21728821.1342 | 15616921.6286
2029 | 19 | 0 | 40457361.2573 | 48451014.3928 | 29385374.8947 | 20601143.2284 | 14537229.8702
2030 | 20 | 0 | 40457361.2573 | 48451014.3928 | 27722051.7874 | 19075132.6189 | 13215663.5184
2031 | 21 | 0 | 40457361.2573 | 48451014.3928 | 26152879.0448 | 17662159.8323 | 12014239.5621
2032 | 22 | 0 | 40457361.2573 | 48451014.3928 | 24672527.4007 | 16353851.6966 | 10922035.9656
2033 | 23 | 0 | 40457361.2573 | 48451014.3928 | 23275969.246 | 15142455.2746 | 9929123.6051
2034 | 24 | 0 | 40457361.2573 | 48451014.3928 | 21958461.5528 | 14020791.921 | 9026476.0046
2035 | 25 | 0 | 40457361.2573 | 48451014.3928 | 20715529.7668 | 12982214.7416 | 8205887.2769
2036 | 26 | 0 | 40457361.2573 | 48451014.3928 | 19542952.6102 | 12020569.2052 | 7459897.5245
2037 | 27 | 0 | 40457361.2573 | 48451014.3928 | 18436747.7454 | 11130156.6715 | 6781725.0223
2038 | 28 | 0 | 40457361.2573 | 48451014.3928 | 17393158.2504 | 10305700.6218 | 6165204.5657
2039 | 29 | 0 | 40457361.2573 | 48451014.3928 | 16408639.8589 | 9542315.3905 | 5604731.4233
2040 | 30 | 0 | 40457361.2573 | 48451014.3928 | 15479848.9235 | 8835477.2134 | 5095210.3849
2041 | 31 | 0 | 40457361.2573 | 48451014.3928 | 14603631.0599 | 8180997.4198 | 4632009.4408
2042 | 32 | 0 | 40457361.2573 | 48451014.3928 | 13777010.4339 | 7574997.611 | 4210917.6734
2043 | 33 | 0 | 40457361.2573 | 48451014.3928 | 12997179.6546 | 7013886.6768 | 3828106.9759
2044 | 34 | 0 | 43898921.8701 | 48451014.3928 | 12736121.1347 | 6745729.3641 | 3614808.5818
2045 | 35 | 0 | 43898921.8701 | 48451014.3928 | 12015208.6176 | 6246045.7075 | 3286189.6199
2046 | 36 | 0 | 43898921.8701 | 48451014.3928 | 11335102.4695 | 5783375.6551 | 2987445.109
2047 | 37 | 0 | 43898921.8701 | 48451014.3928 | 10693492.8957 | 5354977.4584 | 2715859.19
2048 | 38 | 0 | 43898921.8701 | 48451014.3928 | 10088200.845 | 4958312.4615 | 2468962.9
2049 | 39 | 0 | 43898921.8701 | 48451014.3928 | 9517170.6085 | 4591030.0569 | 2244511.7272
2050 | 40 | 0 | 43898921.8701 | 48451014.3928 | 8978462.8382 | 4250953.7564 | 2040465.2066
2051 | 41 | 0 | 43898921.8701 | 48451014.3928 | 8470247.9606 | 3936068.293 | 1854968.3696
2052 | 42 | 0 | 43898921.8701 | 48451014.3928 | 7990799.9628 | 3644507.6787 | 1686334.8815
2053 | 43 | 0 | 43898921.8701 | 48451014.3928 | 7538490.531 | 3374544.1469 | 1533031.7104
2054 | 44 | 0 | 43898921.8701 | 48451014.3928 | 7111783.5198 | 3124577.9138 | 1393665.1913
2055 | 45 | 0 | 43898921.8701 | 48451014.3928 | 6709229.7356 | 2893127.698 | 1266968.3557
2056 | 46 | 0 | 43898921.8701 | 48451014.3928 | 6329462.0148 | 2678821.9426 | 1151789.4143
2057 | 47 | 0 | 43898921.8701 | 48451014.3928 | 5971190.58 | 2480390.6876 | 1047081.2857
2058 | 48 | 0 | 43898921.8701 | 48451014.3928 | 5633198.6603 | 2296658.044 | 951892.0779
2059 | 49 | 0 | 49193068.8684 | 48451014.3928 | 5618993.5606 | 2248443.1616 | 914964.7434
2060 | 50 | 0 | 49193068.8684 | 48451014.3928 | 5300937.3213 | 2081891.8163 | 831786.1304
2061 | 51 | 0 | 49193068.8684 | 48451014.3928 | 5000884.2654 | 1927677.6077 | 756169.2095
2062 | 52 | 0 | 49193068.8684 | 48451014.3928 | 4717815.3447 | 1784886.6738 | 687426.554
2063 | 53 | 0 | 49193068.8684 | 48451014.3928 | 4450769.1931 | 1652672.8461 | 624933.231
2064 | 54 | 0 | 49193068.8684 | 48451014.3928 | 4198838.8615 | 1530252.6353 | 568121.119
2065 | 55 | 0 | 49193068.8684 | 48451014.3928 | 3961168.7372 | 1416900.5882 | 516473.7446
2066 | 56 | 0 | 49193068.8684 | 48451014.3928 | 3736951.6389 | 1311944.9891 | 469521.586
2067 | 57 | 0 | 49193068.8684 | 48451014.3928 | 3525426.0744 | 1214763.8788 | 426837.8054
2068 | 58 | 0 | 49193068.8684 | 48451014.3928 | 3325873.6551 | 1124781.3692 | 388034.3686
2069 | 59 | 0 | 49193068.8684 | 48451014.3928 | 3137616.6558 | 1041464.2308 | 352758.5169
2070 | 60 | 0 | 49193068.8684 | 48451014.3928 | 2960015.713 | 964318.7322 | 320689.5608
2071 | 61 | 0 | 49193068.8684 | 48451014.3928 | 2792467.6538 | 892887.715 | 291535.9644
2072 | 62 | 0 | 49193068.8684 | 48451014.3928 | 2634403.4469 | 826747.8843 | 265032.6949
2073 | 63 | 0 | 49193068.8684 | 48451014.3928 | 2485286.2707 | 765507.3002 | 240938.8135
[5 empty] | 9412892226.1458 | 9076920852.8398 | 8869067326.5205