## Summary
Option 6B Summary
Item | Chainage | Value
Pipeline | 0-8 | 1.9 | m - Diameter
Pump Station | 8 | 50 | m - Pumping Head
Pipeline | 8-22 | 1.9 | m - Diameter
Break Pressure | 22 | 10 | m -Elevation
Pipeline | 22-164 | 1.9 | m - Diameter
Pipeline | 164-226 | 1.8 | m - Diameter
Pipeline | 226-228 | 2 | m - Diameter
Break Pressure | 228 | 10 | m - Elevation
Pump Station | 228 | 120 | m - Pumping Head
Pipeline | 228-274 | 2 | m -Diameter
Break Pressure | 274 | 10 | m - Elevation
Pump Station | 274 | 165 | m - Pumping Head
Pipeline | 274-330 | 2 | m -Diameter
Break Pressure | 330 | 10 | m - Elevation
Pipeline | 330-482 | 1.8 | m -Diameter
Pipeline | 482-500 | 1.5 | m -Diameter
B

## Profile data
Longitudinal profile data - Botswana pipeline
| OPTION 1: Pipeline goes through Serule before joining to BPT1 | OPTION2: Pipeline goes directly to BPT1
CHAINAGE (km0 | NGL (m) | NGL (m) |  | Botswana 1
2 | 1069.018 | 1069.018 | Start | Botswana 2
4 | 1067.321 | 1067.321
6 | 1064.035 | 1064.035
8 | 1063.832 | 1063.832
10 | 1067.893 | 1067.893
12 | 1075.133 | 1075.133
14 | 1082.768 | 1082.768
16 | 1089.726 | 1089.726
18 | 1094.131 | 1094.131
20 | 1097.897 | 1097.897
22 | 1101.67 | 1101.67
24 | 1095.952 | 1095.952
26 | 1090.107 | 1090.107
28 | 1085.781 | 1085.781
30 | 1081.89 | 1081.89
32 | 1077.937 | 1077.937
34 | 1074.89 | 1074.89
36 | 1071.114 | 1071.114
38 | 1065.311 | 1065.311
40 | 1059.051 | 1059.051
42 | 1054.28 | 1054.28
44 | 1053.871 | 1053.871
46 | 1050.42 | 1050.42
48 | 1052.704 | 1052.704
50 | 1056.355 | 1056.355
52 | 1058.466 | 1058.466
54 | 1055.99 | 1055.99
56 | 1055.66 | 1055.66
58 | 1056.404 | 1056.404
60 | 1056.841 | 1056.841
62 | 1056.377 | 1056.377
64 | 1052.503 | 1052.503
66 | 1046.022 | 1046.022
68 | 1036.575 | 1036.575
70 | 1031.818 | 1031.818
72 | 1027.675 | 1027.675
74 | 1023.844 | 1023.844
76 | 1020.888 | 1020.888
78 | 1023.648 | 1023.648
80 | 1027.566 | 1027.566
82 | 1032.371 | 1032.371
84 | 1034.983 | 1034.983
86 | 1033.213 | 1033.213
88 | 1031.188 | 1031.188
90 | 1029.08 | 1029.08
92 | 1026.322 | 1026.322
94 | 1023.207 | 1023.207
96 | 1021.503 | 1021.503
98 | 1019.765 | 1019.765
100 | 1018.493 | 1018.493
102 | 1016.444 | 1016.444
104 | 1013.288 | 1013.288
106 | 1007.843 | 1007.843
108 | 1001.282 | 1001.282
110 | 996.609 | 996.609
112 | 992.999 | 992.999
114 | 993.639 | 993.639
116 | 994.611 | 994.611
118 | 995.751 | 995.751
120 | 996.479 | 996.479
122 | 996.147 | 996.147
124 | 992.094 | 992.094
126 | 985.623 | 985.623
128 | 977.759 | 977.759
130 | 969.772 | 969.772
132 | 981.785 | 981.785
134 | 991.458 | 991.458
136 | 987.77 | 987.77
138 | 982.725 | 982.725
140 | 977.559 | 977.559
142 | 975.289 | 975.289
144 | 973.968 | 973.968
146 | 962.473 | 962.473
148 | 951.285 | 951.285
150 | 948.174 | 948.174
152 | 944.641 | 944.641
154 | 941.566 | 941.566
156 | 940.942 | 940.942
158 | 939.726 | 939.726
160 | 936.738 | 936.738
162 | 933.65 | 933.65
164 | 932.745 | 932.745
166 | 931.696 | 931.696
168 | 930.999 | 930.999
170 | 930.885 | 930.885
172 | 930.378 | 930.378
174 | 931.324 | 931.324
176 | 933.53 | 933.53
178 | 932.714 | 932.714
180 | 928.311 | 928.311
182 | 924.179 | 924.179
184 | 928.398 | 928.398
186 | 930.866 | 930.866
188 | 928.411 | 928.411
190 | 927.849 | 927.849
192 | 926.71 | 926.71
194 | 926.201 | 926.201
196 | 924.509 | 924.509
198 | 923.417 | 923.417
200 | 923.011 | 923.011
202 | 921.969 | 921.969
204 | 920.661 | 920.661
206 | 920.243 | 920.243
208 | 919.297 | 919.297
210 | 917.533 | 917.533
212 | 917.684 | 917.684
214 | 915.724 | 915.724
216 | 915.73 | 915.73
218 | 915.584 | 915.584
220 | 915.444 | 915.444
222 | 913.52 | 913.52
224 | 912.524 | 912.524
226 | 912.565 | 912.565
228 | 913.484 | 913.484
230 | 913.545 | 913.545
232 | 914.546 | 914.546
234 | 918.285 | 918.285
236 | 919.357 | 919.357
238 | 918.649 | 918.649
240 | 922.974 | 922.974
242 | 927.375 | 927.375
244 | 929.253 | 929.253
246 | 930.863 | 930.863
248 | 931.924 | 931.924
250 | 936.722 | 936.722
252 | 941.777 | 941.777
254 | 948.143 | 948.143
256 | 955.417 | 955.417
258 | 962.7 | 962.7
260 | 969.281 | 969.281
262 | 980.284 | 980.284
264 | 986.551 | 986.551
266 | 989.198 | 989.198
268 | 994.39 | 994.39
270 | 999.917 | 999.917
272 | 1004.623 | 1004.623
274 | 1008.819 | 1008.819
276 | 1007.834 | 1007.834
278 | 1005.626 | 1005.626
280 | 1001.623 | 1001.623
282 | 1004.052 | 1004.052
284 | 1010.797 | 1010.797
286 | 1014.67 | 1014.67
288 | 1017.319 | 1017.319
290 | 1027.459 | 1027.459
292 | 1031.99 | 1031.99
294 | 1036.254 | 1036.254
296 | 1040.127 | 1040.127
298 | 1044.396 | 1044.396
300 | 1051.339 | 1051.339
302 | 1060.955 | 1060.955
304 | 1070.227 | 1070.227
306 | 1072.691 | 1072.691
308 | 1076.503 | 1076.503
310 | 1083.996 | 1083.996
312 | 1097.188 | 1097.188
314 | 1103.545 | 1103.545
316 | 1105.174 | 1105.174
318 | 1111.657 | 1111.657
320 | 1122.935 | 1122.935
322 | 1128.197 | 1128.197
324 | 1132.561 | 1132.561
326 | 1131.854 | 1131.854
328 | 1133.338 | 1133.338
330 | 1136.405 | 1136.405
332 | 1128.709 | 1128.709
334 | 1120.713 | 1120.713
336 | 1115.226 | 1115.226
338 | 1108.709 | 1108.709
340 | 1102.499 | 1102.499
342 | 1096.349 | 1096.349
344 | 1090.39 | 1090.39
346 | 1087.765 | 1087.765
348 | 1084.661 | 1084.661
350 | 1081.662 | 1081.662
352 | 1076.872 | 1076.872
354 | 1070.898 | 1070.898
356 | 1065.018 | 1065.018
358 | 1059.58 | 1059.58
360 | 1055.284 | 1055.284
362 | 1050.886 | 1050.886
364 | 1052.647 | 1052.647
366 | 1051.117 | 1051.117
368 | 1048.266 | 1048.266
370 | 1040.172 | 1040.172
372 | 1033.483 | 1033.483
374 | 1030.95 | 1030.95
376 | 1032.263 | 1032.263
378 | 1031.391 | 1031.391
380 | 1025.791 | 1025.791
382 | 1020.911 | 1020.911
384 | 1015.65 | 1015.65
386 | 1012.139 | 1012.139
388 | 1010.472 | 1010.472
390 | 1005.401 | 1005.401
392 | 996.666 | 996.666
394 | 991.35 | 991.35
396 | 990.486 | 990.486
398 | 992.761 | 992.761
400 | 999.077 | 999.077
402 | 1001.8 | 1001.8
404 | 1002.224 | 1002.224
406 | 1002.003 | 1002.003
408 | 1003.596 | 1003.596
410 | 994.111 | 994.111
412 | 983.925 | 983.925
414 | 972.347 | 972.347
416 | 963.901 | 963.901
418 | 963.258 | 963.258
420 | 965.836 | 965.872
422 | 966.309 | 966.177
424 | 972.884 | 973.825
426 | 983.972 | 983.972
428 | 994.096 | 994.096
430 | 991.695 | 991.695
432 | 984.933 | 984.933
434 | 978.185 | 974.509
436 | 972.686 | 966.698
438 | 966.824 | 963.618
440 | 960.902 | 957.803
442 | 952.924 | 954.277
444 | 945.683 | 947.182
446 | 941.042 | 938.045
448 | 937.104 | 930.871
450 | 939.943 | 926.391
452 | 944.776 | 918.344
454 | 947.762 | 911.505
456 | 952.649 | 903.61
458 | 954.554 | 900.63
460 | 952.37 | 904.066
462 | 947.552 | 915.092
464 | 941.898 | 905.556
466 | 940.521 | 905.271
468 | 939.702 | 901.918
470 | 937.147 | 895.651
472 | 933.872 | 892.304
474 | 933.184 | 895.279
476 | 939.292 | 896.818
478 | 944.619 | 909.921
480 | 954.023 | 926.295
482 | 968.263 | 924.888
484 | 970.384 | 919.044
486 | 964.636 | 911.164
488 | 956.631 | 903.893
490 | 947.426 | 901.953
492 | 941.72 | 900.198
494 | 935.985 | 904.177
496 | 930.475 | 912.253
498 | 927.611 | 915.297
500 | 931.256 | 919.629
502 | 920.044
504 | 911.78
506 | 907.989
508 | 907.289
510 | 900.577
512 | 902.112
514 | 900.179
516 | 903.811
518 | 910.027
520 | 911.131 |  | End

## Flow Rate Calculations
Estimated Transfer Rate Demand | 100 | Mm3/a
Availible Days | 365
Pumping Hours | 24
Pf | 1.052
Pl | 1.02
PR | 1.2
Peak Design Flow | 4.0831 | m3/s

## Calculation Constants
Friction Factors
Ks (mm) - New | 0.03
Ks (mm) - Average | 0.06
Ks (mm) - Old | 0.15
Ks (mm) - Biofilm | 0.5
Kinemeatic Viscosity | 1.13e-06 | m2/s
Minor Loss - k | 150
Grade of Steel | X42
Yeild Capacity | 300 | Mpa
Design % of Yeild | 50%
Minimum D/t ratio | 160 | mm/mm

## Hydraulics
Option 6B |  |  |  | Option 6B | [12 empty] | Option 6B
Pump Station |  |  |  | Pipe Line | [9 empty] | Steel Pipeline Design |  |  | New Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Average Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Old Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Biofilm Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes
Name | Chainage (km) | Elevation (m) | Pumped Head (m) | Reference | Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Flow Rate (m3/s) | PipeVelocity (m/s) | Re | Static Head (m) | Dynamic Head (m) | Design Pressure (m) | Pipe Wall thickness (mm) | Steel Mass (kg) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m)
PS 1 | 8 | 1063.832 | 50 | Reservoir | 2 | 1069.018 | 0 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 10 | 10 | 10 | 11.875 | 0 | 0.00867 |  |  | 0 | 0 | 10 | 1079.018 | 0.0097304 |  |  | 0 | 0 | 10 | 1079.018 | 0.011459 |  |  | 0 | 0 | 10 | 1079.018 | 0.014543 |  |  | 0 | 0 | 10 | 1079.018
PS 3 | 228 | 913.484 | 120 |  | 4 | 1067.321 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 11.697 | 10.6689 | 11.697 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 10.6689 | 1077.9899 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 10.5509 | 1077.8719 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 10.3586 | 1077.6796 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 10.0086 | 1077.3296
PS 2 | 274 | 1008.819 | 165 |  | 6 | 1064.035 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 14.983 | 12.9268 | 14.983 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 12.9268 | 1076.9618 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 12.6908 | 1076.7258 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 12.3062 | 1076.3412 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 11.6062 | 1075.6412
|  |  |  | Pump Station | 8 | 1063.832 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 62.1017 | 61.7477 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 50 | 62.1017 | 1125.9337 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 50 | 61.7477 | 1125.5797 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 50 | 61.1707 | 1125.0027 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 50 | 60.1208 | 1123.9528
[5 empty] | 10 | 1067.893 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 57.0126 | 56.5407 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 57.0126 | 1124.9056 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 56.5407 | 1124.4337 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 55.7713 | 1123.6643 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 54.3714 | 1122.2644
Reservoirs |  |  |  |  | 12 | 1075.133 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 48.7445 | 48.1546 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 48.7445 | 1123.8775 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 48.1546 | 1123.2876 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 47.1929 | 1122.3259 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 45.443 | 1120.576
Name | Chainage (km) | Water Elevation (m) | Height |  | 14 | 1082.768 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 40.0814 | 39.3735 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 40.0814 | 1122.8494 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 39.3735 | 1122.1415 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 38.2195 | 1120.9875 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 36.1196 | 1118.8876
Supply Resrvoir | 2 | 1079.018 | 10 |  | 16 | 1089.726 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 32.0953 | 31.2694 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 32.0953 | 1121.8213 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 31.2694 | 1120.9954 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 29.9231 | 1119.6491 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.4732 | 1117.1992
BPT 3 | 22 | 1111.67 | 10 |  | 18 | 1094.131 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 26.6622 | 25.7183 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 26.6622 | 1120.7932 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 25.7183 | 1119.8493 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 24.1796 | 1118.3106 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 21.3798 | 1115.5108
BPT 5 | 228 | 923.484 | 10 |  | 20 | 1097.897 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 21.8681 | 20.8062 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 21.8681 | 1119.7651 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 20.8062 | 1118.7032 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 19.0752 | 1116.9722 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 15.9254 | 1113.8224
BPT 4 | 274 | 1018.819 | 10 | Reservoir | 22 | 1101.67 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 10 | 10 | 10 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 10 | 1111.67 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 10 | 1111.67 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 10 | 1111.67 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 10 | 1111.67
BPT 2 | 330 | 1146.405 | 10 |  | 24 | 1095.952 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 15.718 | 14.6899 | 15.718 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 14.6899 | 1110.6419 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 14.5719 | 1110.5239 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 14.3796 | 1110.3316 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 14.0296 | 1109.9816
BPT 1 | 500 | 929.629 | 10 |  | 26 | 1090.107 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 21.563 | 19.5068 | 21.563 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 19.5068 | 1109.6138 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 19.2708 | 1109.3778 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 18.8862 | 1108.9932 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 18.1862 | 1108.2932
[5 empty] | 28 | 1085.781 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 25.889 | 22.8047 | 25.889 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 22.8047 | 1108.5857 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 22.4507 | 1108.2317 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 21.8737 | 1107.6547 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 20.8238 | 1106.6048
|  | -127.586 |  |  | 30 | 1081.89 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 29.78 | 25.6676 | 29.78 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 25.6676 | 1107.5576 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 25.1957 | 1107.0857 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 24.4263 | 1106.3163 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 23.0264 | 1104.9164
[5 empty] | 32 | 1077.937 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 33.733 | 28.5925 | 33.733 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 28.5925 | 1106.5295 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 28.0026 | 1105.9396 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 27.0409 | 1104.9779 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 25.291 | 1103.228
[5 empty] | 34 | 1074.89 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 36.78 | 30.6114 | 36.78 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 30.6114 | 1105.5014 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 29.9035 | 1104.7935 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 28.7495 | 1103.6395 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 26.6496 | 1101.5396
[5 empty] | 36 | 1071.114 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 40.556 | 33.3593 | 40.556 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 33.3593 | 1104.4733 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 32.5334 | 1103.6474 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 31.1871 | 1102.3011 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 28.7372 | 1099.8512
Route | Botswana 2 |  |  |  | 38 | 1065.311 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 46.359 | 38.1342 | 46.359 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 38.1342 | 1103.4452 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 37.1903 | 1102.5013 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 35.6516 | 1100.9626 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 32.8518 | 1098.1628
Option | 6B |  |  |  | 40 | 1059.051 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 52.619 | 43.3661 | 52.619 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 43.3661 | 1102.4171 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 42.3042 | 1101.3552 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 40.5732 | 1099.6242 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 37.4234 | 1096.4744
[5 empty] | 42 | 1054.28 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 57.39 | 47.109 | 57.39 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 47.109 | 1101.389 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 45.9292 | 1100.2092 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 44.0058 | 1098.2858 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 40.506 | 1094.786
[5 empty] | 44 | 1053.871 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 57.799 | 46.4899 | 57.799 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 46.4899 | 1100.3609 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 45.1921 | 1099.0631 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 43.0764 | 1096.9474 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 39.2267 | 1093.0977
[5 empty] | 46 | 1050.42 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 61.25 | 48.9128 | 61.25 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 48.9128 | 1099.3328 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 47.497 | 1097.917 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 45.1889 | 1095.6089 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 40.9893 | 1091.4093
[5 empty] | 48 | 1052.704 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 58.966 | 45.6007 | 58.966 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 45.6007 | 1098.3047 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 44.0669 | 1096.7709 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 41.5665 | 1094.2705 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 37.0169 | 1089.7209
[5 empty] | 50 | 1056.355 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.315 | 40.9216 | 55.315 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 40.9216 | 1097.2766 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 39.2698 | 1095.6248 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 36.5771 | 1092.9321 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 31.6775 | 1088.0325
[5 empty] | 52 | 1058.466 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 53.204 | 37.7825 | 53.204 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 37.7825 | 1096.2485 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 36.0127 | 1094.4787 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 33.1277 | 1091.5937 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.8781 | 1086.3441
[5 empty] | 54 | 1055.99 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.68 | 39.2304 | 55.68 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 39.2304 | 1095.2204 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 37.3426 | 1093.3326 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 34.2653 | 1090.2553 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 28.6657 | 1084.6557
[5 empty] | 56 | 1055.66 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 56.01 | 38.5323 | 56.01 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 38.5323 | 1094.1923 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 36.5266 | 1092.1866 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 33.2568 | 1088.9168 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.3073 | 1082.9673
[5 empty] | 58 | 1056.404 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.266 | 36.7602 | 55.266 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 36.7602 | 1093.1642 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 34.6365 | 1091.0405 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 31.1744 | 1087.5784 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 24.8749 | 1081.2789
[5 empty] | 60 | 1056.841 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 54.829 | 35.2951 | 54.829 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 35.2951 | 1092.1361 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 33.0534 | 1089.8944 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 29.399 | 1086.24 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 22.7495 | 1079.5905
[5 empty] | 62 | 1056.377 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.293 | 34.731 | 55.293 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 34.731 | 1091.108 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 32.3713 | 1088.7483 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 28.5246 | 1084.9016 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 21.5251 | 1077.9021
[5 empty] | 64 | 1052.503 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 59.167 | 37.5769 | 59.167 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 37.5769 | 1090.0799 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 35.0992 | 1087.6022 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 31.0602 | 1083.5632 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 23.7107 | 1076.2137
[5 empty] | 66 | 1046.022 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 65.648 | 43.0298 | 65.648 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 43.0298 | 1089.0518 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 40.4341 | 1086.4561 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 36.2027 | 1082.2247 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 28.5033 | 1074.5253
[5 empty] | 68 | 1036.575 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 75.095 | 51.4487 | 75.095 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 51.4487 | 1088.0237 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 48.735 | 1085.31 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 44.3113 | 1080.8863 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 36.2619 | 1072.8369
[5 empty] | 70 | 1031.818 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 79.852 | 55.1776 | 79.852 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 55.1776 | 1086.9956 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 52.346 | 1084.164 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 47.7299 | 1079.5479 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 39.3305 | 1071.1485
[5 empty] | 72 | 1027.675 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 83.995 | 58.2925 | 83.995 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 58.2925 | 1085.9675 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 55.3429 | 1083.0179 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 50.5345 | 1078.2095 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 41.7851 | 1069.4601
[5 empty] | 74 | 1023.844 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 87.826 | 61.0954 | 87.826 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 61.0954 | 1084.9394 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 58.0278 | 1081.8718 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 53.0271 | 1076.8711 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 43.9277 | 1067.7717
[5 empty] | 76 | 1020.888 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 90.782 | 63.0233 | 90.782 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 63.0233 | 1083.9113 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 59.8377 | 1080.7257 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 54.6446 | 1075.5326 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 45.1953 | 1066.0833
[5 empty] | 78 | 1023.648 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 88.022 | 59.2352 | 88.022 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 59.2352 | 1082.8832 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 55.9316 | 1079.5796 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 50.5462 | 1074.1942 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 40.7469 | 1064.3949
[5 empty] | 80 | 1027.566 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 84.104 | 54.2891 | 84.104 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 54.2891 | 1081.8551 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 50.8675 | 1078.4335 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 45.2898 | 1072.8558 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 35.1405 | 1062.7065
[5 empty] | 82 | 1032.371 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 79.299 | 48.456 | 79.299 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 48.456 | 1080.827 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 44.9165 | 1077.2875 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 39.1464 | 1071.5174 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 28.6471 | 1061.0181
[5 empty] | 84 | 1034.983 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 76.687 | 44.8159 | 76.687 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 44.8159 | 1079.7989 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 41.1584 | 1076.1414 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 35.1959 | 1070.1789 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 24.3468 | 1059.3298
[5 empty] | 86 | 1033.213 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 78.457 | 45.5578 | 78.457 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 45.5578 | 1078.7708 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 41.7823 | 1074.9953 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 35.6275 | 1068.8405 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 24.4284 | 1057.6414
[5 empty] | 88 | 1031.188 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 80.482 | 46.5547 | 80.482 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 46.5547 | 1077.7427 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 42.6612 | 1073.8492 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 36.3141 | 1067.5021 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 24.765 | 1055.953
[5 empty] | 90 | 1029.08 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 82.59 | 47.6346 | 82.59 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 47.6346 | 1076.7146 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 43.6231 | 1072.7031 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 37.0837 | 1066.1637 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 25.1846 | 1054.2646
[5 empty] | 92 | 1026.322 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 85.348 | 49.3645 | 85.348 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 49.3645 | 1075.6865 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 45.235 | 1071.557 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 38.5033 | 1064.8253 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 26.2542 | 1052.5762
[5 empty] | 94 | 1023.207 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 88.463 | 51.4514 | 88.463 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 51.4514 | 1074.6584 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 47.2039 | 1070.4109 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 40.2798 | 1063.4868 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.6808 | 1050.8878
[5 empty] | 96 | 1021.503 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 90.167 | 52.1273 | 90.167 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 52.1273 | 1073.6303 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 47.7619 | 1069.2649 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 40.6454 | 1062.1484 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.6964 | 1049.1994
[5 empty] | 98 | 1019.765 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 91.905 | 52.8372 | 91.905 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 52.8372 | 1072.6022 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 48.3538 | 1068.1188 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 41.045 | 1060.81 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.746 | 1047.511
[5 empty] | 100 | 1018.493 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 93.177 | 53.0811 | 93.177 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 53.0811 | 1071.5741 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 48.4797 | 1066.9727 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 40.9786 | 1059.4716 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.3296 | 1045.8226
[5 empty] | 102 | 1016.444 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 95.226 | 54.102 | 95.226 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 54.102 | 1070.546 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 49.3826 | 1065.8266 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 41.6892 | 1058.1332 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.6902 | 1044.1342
[5 empty] | 104 | 1013.288 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 98.382 | 56.2299 | 98.382 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 56.2299 | 1069.5179 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 51.3925 | 1064.6805 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 43.5067 | 1056.7947 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 29.1578 | 1042.4458
[5 empty] | 106 | 1007.843 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 103.827 | 60.6468 | 103.827 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 60.6468 | 1068.4898 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 55.6914 | 1063.5344 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 47.6133 | 1055.4563 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 32.9144 | 1040.7574
[5 empty] | 108 | 1001.282 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 110.388 | 66.1797 | 110.388 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 66.1797 | 1067.4617 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 61.1063 | 1062.3883 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 52.8359 | 1054.1179 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 37.787 | 1039.069
[5 empty] | 110 | 996.609 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.061 | 69.8246 | 115.061 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 69.8246 | 1066.4336 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 64.6333 | 1061.2423 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 56.1705 | 1052.7795 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 40.7716 | 1037.3806
[5 empty] | 112 | 992.999 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 118.671 | 72.4065 | 118.671 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 72.4065 | 1065.4055 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 67.0972 | 1060.0962 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 58.4421 | 1051.4411 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 42.6932 | 1035.6922
[5 empty] | 114 | 993.639 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 118.031 | 70.7384 | 118.031 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 70.7384 | 1064.3774 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 65.3111 | 1058.9501 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 56.4636 | 1050.1026 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 40.3648 | 1034.0038
[5 empty] | 116 | 994.611 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 117.059 | 68.7383 | 117.059 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 68.7383 | 1063.3493 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 63.193 | 1057.804 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 54.1532 | 1048.7642 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 37.7044 | 1032.3154
[5 empty] | 118 | 995.751 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.919 | 66.5702 | 115.919 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 66.5702 | 1062.3212 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 60.9069 | 1056.6579 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 51.6748 | 1047.4258 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 34.876 | 1030.627
[5 empty] | 120 | 996.479 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.191 | 64.8141 | 115.191 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 64.8141 | 1061.2931 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 59.0328 | 1055.5118 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 49.6084 | 1046.0874 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 32.4596 | 1028.9386
[5 empty] | 122 | 996.147 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.523 | 64.118 | 115.523 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 64.118 | 1060.265 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 58.2188 | 1054.3658 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 48.602 | 1044.749 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 31.1032 | 1027.2502
[5 empty] | 124 | 992.094 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 119.576 | 67.1429 | 119.576 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 67.1429 | 1059.2369 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 61.1257 | 1053.2197 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 51.3165 | 1043.4105 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 33.4679 | 1025.5619
[5 empty] | 126 | 985.623 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 126.047 | 72.5858 | 126.047 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 72.5858 | 1058.2088 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 66.4506 | 1052.0736 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 56.4491 | 1042.0721 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 38.2505 | 1023.8735
[5 empty] | 128 | 977.759 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 133.911 | 79.4217 | 133.911 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 79.4217 | 1057.1807 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 73.1685 | 1050.9275 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 62.9747 | 1040.7337 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 44.4261 | 1022.1851
[5 empty] | 130 | 969.772 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 141.898 | 86.3806 | 141.898 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 86.3806 | 1056.1526 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 80.0094 | 1049.7814 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 69.6233 | 1039.3953 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 50.7247 | 1020.4967
[5 empty] | 132 | 981.785 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 129.885 | 73.3395 | 129.885 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 73.3395 | 1055.1245 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 66.8503 | 1048.6353 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 56.2718 | 1038.0568 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 37.0233 | 1018.8083
[5 empty] | 134 | 991.458 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 120.212 | 62.6384 | 120.212 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 62.6384 | 1054.0964 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 56.0312 | 1047.4892 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 45.2604 | 1036.7184 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 25.6619 | 1017.1199
[5 empty] | 136 | 987.77 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 123.9 | 65.2983 | 123.9 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 65.2983 | 1053.0683 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 58.5732 | 1046.3432 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 47.61 | 1035.38 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 27.6615 | 1015.4315
[5 empty] | 138 | 982.725 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 128.945 | 69.3152 | 128.945 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 69.3152 | 1052.0402 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 62.4721 | 1045.1971 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 51.3166 | 1034.0416 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 31.0181 | 1013.7431
[5 empty] | 140 | 977.559 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 134.111 | 73.4531 | 134.111 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 73.4531 | 1051.0121 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 66.492 | 1044.051 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 55.1442 | 1032.7032 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 34.4957 | 1012.0547
[5 empty] | 142 | 975.289 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 136.381 | 74.695 | 136.381 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 74.695 | 1049.984 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 67.6159 | 1042.9049 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 56.0757 | 1031.3647 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 35.0773 | 1010.3663
[5 empty] | 144 | 973.968 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 137.702 | 74.9879 | 137.702 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 74.9879 | 1048.9559 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 67.7908 | 1041.7588 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 56.0583 | 1030.0263 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 34.7099 | 1008.6779
[5 empty] | 146 | 962.473 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 149.197 | 85.4548 | 149.197 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 85.4548 | 1047.9278 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 78.1397 | 1040.6127 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 66.2149 | 1028.6879 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 44.5165 | 1006.9895
[5 empty] | 148 | 951.285 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 160.385 | 95.6147 | 160.385 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 95.6147 | 1046.8997 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 88.1816 | 1039.4666 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 76.0645 | 1027.3495 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 54.0161 | 1005.3011
[5 empty] | 150 | 948.174 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 163.496 | 97.6976 | 163.496 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 97.6976 | 1045.8716 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 90.1466 | 1038.3206 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 77.8371 | 1026.0111 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 55.4387 | 1003.6127
[5 empty] | 152 | 944.641 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 167.029 | 100.2025 | 167.029 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 100.2025 | 1044.8435 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 92.5335 | 1037.1745 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 80.0316 | 1024.6726 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 57.2833 | 1001.9243
[5 empty] | 154 | 941.566 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 170.104 | 102.2494 | 170.104 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 102.2494 | 1043.8154 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 94.4624 | 1036.0284 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 81.7682 | 1023.3342 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 58.6699 | 1000.2359
[5 empty] | 156 | 940.942 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 170.728 | 101.8453 | 170.728 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 101.8453 | 1042.7873 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 93.9403 | 1034.8823 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 81.0538 | 1021.9958 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 57.6055 | 998.5475
[5 empty] | 158 | 939.726 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 171.944 | 102.0332 | 171.944 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 102.0332 | 1041.7592 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 94.0102 | 1033.7362 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 80.9314 | 1020.6574 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 57.1331 | 996.8591
[5 empty] | 160 | 936.738 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 174.932 | 103.9931 | 174.932 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 103.9931 | 1040.7311 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 95.8521 | 1032.5901 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 82.581 | 1019.319 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 58.4327 | 995.1707
[5 empty] | 162 | 933.65 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 178.02 | 106.053 | 178.02 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.063422 | 1.0281 | 0 | 106.053 | 1039.703 | 0.0097304 | 1.0827 | 0.063422 | 1.1461 | 0 | 97.7941 | 1031.4441 | 0.011459 | 1.275 | 0.063422 | 1.3384 | 0 | 84.3305 | 1017.9805 | 0.014543 | 1.625 | 0.063422 | 1.6884 | 0 | 59.8323 | 993.4823
[5 empty] | 164 | 932.745 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.925 | 105.604 | 178.925 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 105.604 | 1038.349 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 97.1884 | 1029.9334 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 83.4691 | 1016.2141 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 58.5043 | 991.2493
[5 empty] | 166 | 931.696 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 179.974 | 105.299 | 179.974 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 105.299 | 1036.995 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 96.7267 | 1028.4227 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 82.7517 | 1014.4477 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 57.3203 | 989.0163
[5 empty] | 168 | 930.999 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.671 | 104.642 | 180.671 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 104.642 | 1035.641 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 95.913 | 1026.912 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 81.6823 | 1012.6813 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.7842 | 986.7832
[5 empty] | 170 | 930.885 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.785 | 103.402 | 180.785 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 103.402 | 1034.287 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 94.5163 | 1025.4013 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 80.0298 | 1010.9148 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 53.6652 | 984.5502
[5 empty] | 172 | 930.378 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 181.292 | 102.5551 | 181.292 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 102.5551 | 1032.9331 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 93.5126 | 1023.8906 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 78.7704 | 1009.1484 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 51.9391 | 982.3171
[5 empty] | 174 | 931.324 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.346 | 100.2551 | 180.346 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 100.2551 | 1031.5791 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 91.0559 | 1022.3799 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 76.058 | 1007.382 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 48.7601 | 980.0841
[5 empty] | 176 | 933.53 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.14 | 96.6951 | 178.14 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 96.6951 | 1030.2251 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 87.3392 | 1020.8692 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 72.0856 | 1005.6156 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 44.321 | 977.851
[5 empty] | 178 | 932.714 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.956 | 96.1571 | 178.956 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 96.1571 | 1028.8711 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 86.6445 | 1019.3585 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 71.1351 | 1003.8491 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 42.904 | 975.618
[5 empty] | 180 | 928.311 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.359 | 99.2061 | 183.359 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 99.2061 | 1027.5171 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 89.5368 | 1017.8478 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 73.7717 | 1002.0827 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 45.0739 | 973.3849
[5 empty] | 182 | 924.179 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 187.491 | 101.9842 | 187.491 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 101.9842 | 1026.1632 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 92.1581 | 1016.3371 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 76.1373 | 1000.3163 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 46.9729 | 971.1519
[5 empty] | 184 | 928.398 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.272 | 96.4112 | 183.272 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 96.4112 | 1024.8092 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 86.4284 | 1014.8264 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 70.1519 | 998.5499 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 40.5209 | 968.9189
[5 empty] | 186 | 930.866 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.804 | 92.5892 | 180.804 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.5892 | 1023.4552 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 82.4497 | 1013.3157 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 65.9174 | 996.7834 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 35.8198 | 966.6858
[5 empty] | 188 | 928.411 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.259 | 93.6902 | 183.259 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 93.6902 | 1022.1012 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 83.394 | 1011.805 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 66.606 | 995.017 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 36.0418 | 964.4528
[5 empty] | 190 | 927.849 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.821 | 92.8982 | 183.821 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.8982 | 1020.7472 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 82.4453 | 1010.2943 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 65.4016 | 993.2506 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 34.3707 | 962.2197
[5 empty] | 192 | 926.71 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 184.96 | 92.6832 | 184.96 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.6832 | 1019.3932 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 82.0736 | 1008.7836 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 64.7742 | 991.4842 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 33.2767 | 959.9867
[5 empty] | 194 | 926.201 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 185.469 | 91.8383 | 185.469 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 91.8383 | 1018.0393 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 81.0719 | 1007.2729 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 63.5167 | 989.7177 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 31.5526 | 957.7536
[5 empty] | 196 | 924.509 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 187.161 | 92.1763 | 187.161 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.1763 | 1016.6853 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 81.2532 | 1005.7622 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 63.4423 | 987.9513 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 31.0116 | 955.5206
[5 empty] | 198 | 923.417 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 188.253 | 91.9143 | 188.253 | 11.2952 | 996509.3057 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 91.9143 | 1015.3313 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 80.8345 | 1004.2515 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 62.7679 | 986.1849 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 29.8705 | 953.2875
[5 empty] | 200 | 923.011 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 188.659 | 90.9663 | 188.659 | 11.3195 | 998644.849 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 90.9663 | 1013.9773 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.7298 | 1002.7408 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 61.4075 | 984.4185 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 28.0435 | 951.0545
[5 empty] | 202 | 921.969 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 189.701 | 90.6543 | 189.701 | 11.3821 | 1004125.4583 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 90.6543 | 1012.6233 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.2611 | 1001.2301 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 60.683 | 982.652 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 26.8525 | 948.8215
[5 empty] | 204 | 920.661 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 191.009 | 90.6084 | 191.009 | 11.4605 | 1011004.6025 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 90.6084 | 1011.2694 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.0584 | 999.7194 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 60.2246 | 980.8856 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 25.9274 | 946.5884
[5 empty] | 206 | 920.243 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 191.427 | 89.6724 | 191.427 | 11.4856 | 1013202.8554 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 89.6724 | 1009.9154 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 77.9657 | 998.2087 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 58.8762 | 979.1192 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 24.1124 | 944.3554
[5 empty] | 208 | 919.297 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 192.373 | 89.2644 | 192.373 | 11.5424 | 1018177.6195 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 89.2644 | 1008.5614 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 77.401 | 996.698 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 58.0558 | 977.3528 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 22.8253 | 942.1223
[5 empty] | 210 | 917.533 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 194.137 | 89.6744 | 194.137 | 11.6482 | 1027453.1808 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 89.6744 | 1007.2074 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 77.6543 | 995.1873 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 58.0533 | 975.5863 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 22.3563 | 939.8893
[5 empty] | 212 | 917.684 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 193.986 | 88.1694 | 193.986 | 11.6392 | 1026659.2276 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 88.1694 | 1005.8534 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 75.9926 | 993.6766 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 56.1359 | 973.8199 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 19.9722 | 937.6562
[5 empty] | 214 | 915.724 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 195.946 | 88.7754 | 195.946 | 11.7568 | 1036964.2159 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 88.7754 | 1004.4994 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 76.4419 | 992.1659 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 56.3295 | 972.0535 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 19.6992 | 935.4232
[5 empty] | 216 | 915.73 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 195.94 | 87.4155 | 195.94 | 11.7564 | 1036932.6721 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 87.4155 | 1003.1455 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 74.9252 | 990.6552 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 54.5571 | 970.2871 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 17.4601 | 933.1901
[5 empty] | 218 | 915.584 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 196.086 | 86.2075 | 196.086 | 11.7652 | 1037700.2343 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 86.2075 | 1001.7915 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 73.5605 | 989.1445 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 52.9366 | 968.5206 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 15.3731 | 930.9571
[5 empty] | 220 | 915.444 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 196.226 | 84.9935 | 196.226 | 11.7736 | 1038436.2457 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 84.9935 | 1000.4375 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 72.1898 | 987.6338 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 51.3102 | 966.7542 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 13.2801 | 928.7241
[5 empty] | 222 | 913.52 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 198.15 | 85.5635 | 198.15 | 11.889 | 1048550.4405 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 85.5635 | 999.0835 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 72.6031 | 986.1231 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 51.4678 | 964.9878 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 12.971 | 926.491
[5 empty] | 224 | 912.524 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 199.146 | 85.2055 | 199.146 | 11.9488 | 1053785.7546 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 85.2055 | 997.7295 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 72.0884 | 984.6124 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 50.6974 | 963.2214 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 11.734 | 924.258
[5 empty] | 226 | 912.565 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | 199.105 | 84.3726 | 199.105 | 13.2737 | 1300704.0144 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 84.3726 | 996.9376 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 71.1653 | 983.7303 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 49.6275 | 962.1925 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 10.3977 | 922.9627
|  |  |  | Reservoir | 228 | 913.484 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 10 | 130 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 120 | 10 | 1043.484 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 120 | 130 | 1043.484 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 120 | 130 | 1043.484 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 120 | 130 | 1043.484
[5 empty] | 230 | 913.545 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 129.147 | 129.0569 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 129.147 | 1042.692 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 129.0569 | 1042.6019 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 128.9101 | 1042.4551 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 128.6437 | 1042.1887
[5 empty] | 232 | 914.546 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 127.3541 | 127.1738 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 127.3541 | 1041.9001 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 127.1738 | 1041.7198 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 126.8802 | 1041.4262 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 126.3474 | 1040.8934
[5 empty] | 234 | 918.285 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 122.8231 | 122.5527 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 122.8231 | 1041.1081 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 122.5527 | 1040.8377 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 122.1123 | 1040.3973 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 121.3131 | 1039.5981
[5 empty] | 236 | 919.357 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 120.9592 | 120.5987 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 120.9592 | 1040.3162 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 120.5987 | 1039.9557 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 120.0115 | 1039.3685 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 118.9458 | 1038.3028
[5 empty] | 238 | 918.649 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 120.8752 | 120.4246 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 120.8752 | 1039.5242 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 120.4246 | 1039.0736 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 119.6906 | 1038.3396 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 118.3585 | 1037.0075
[5 empty] | 240 | 922.974 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 115.7583 | 115.2175 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 115.7583 | 1038.7323 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 115.2175 | 1038.1915 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 114.3367 | 1037.3107 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 112.7381 | 1035.7121
[5 empty] | 242 | 927.375 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 110.5653 | 109.9344 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 110.5653 | 1037.9403 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 109.9344 | 1037.3094 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 108.9068 | 1036.2818 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 107.0418 | 1034.4168
[5 empty] | 244 | 929.253 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 107.8954 | 107.1743 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 107.8954 | 1037.1484 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 107.1743 | 1036.4273 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 105.9999 | 1035.2529 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 103.8685 | 1033.1215
[5 empty] | 246 | 930.863 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 105.4934 | 104.6822 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 105.4934 | 1036.3564 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 104.6822 | 1035.5452 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 103.361 | 1034.224 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 100.9632 | 1031.8262
[5 empty] | 248 | 931.924 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 103.6405 | 102.7391 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 103.6405 | 1035.5645 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 102.7391 | 1034.6631 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 101.2712 | 1033.1952 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 98.6069 | 1030.5309
[5 empty] | 250 | 936.722 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 98.0505 | 97.059 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 98.0505 | 1034.7725 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 97.059 | 1033.781 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 95.4443 | 1032.1663 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 92.5136 | 1029.2356
[5 empty] | 252 | 941.777 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 92.2036 | 91.122 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 92.2036 | 1033.9806 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 91.122 | 1032.899 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 89.3604 | 1031.1374 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 86.1633 | 1027.9403
[5 empty] | 254 | 948.143 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 85.0456 | 83.8739 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 85.0456 | 1033.1886 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 83.8739 | 1032.0169 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 81.9655 | 1030.1085 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 78.502 | 1026.645
[5 empty] | 256 | 955.417 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 76.9797 | 75.7178 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 76.9797 | 1032.3967 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 75.7178 | 1031.1348 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 73.6626 | 1029.0796 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 69.9327 | 1025.3497
[5 empty] | 258 | 962.7 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 68.9047 | 67.5527 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 68.9047 | 1031.6047 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 67.5527 | 1030.2527 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 65.3507 | 1028.0507 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 61.3544 | 1024.0544
[5 empty] | 260 | 969.281 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 61.5318 | 60.0896 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 61.5318 | 1030.8128 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 60.0896 | 1029.3706 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 57.7409 | 1027.0219 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 53.478 | 1022.759
[5 empty] | 262 | 980.284 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 49.7368 | 48.2045 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 49.7368 | 1030.0208 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 48.2045 | 1028.4885 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 45.709 | 1025.993 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 41.1797 | 1021.4637
[5 empty] | 264 | 986.551 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 42.6779 | 41.0554 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 42.6779 | 1029.2289 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 41.0554 | 1027.6064 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 38.4131 | 1024.9641 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 33.6174 | 1020.1684
[5 empty] | 266 | 989.198 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 39.2389 | 37.5264 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 39.2389 | 1028.4369 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 37.5264 | 1026.7244 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 34.7372 | 1023.9352 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 29.6751 | 1018.8731
[5 empty] | 268 | 994.39 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 33.255 | 31.4523 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 33.255 | 1027.645 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 31.4523 | 1025.8423 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 28.5163 | 1022.9063 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 23.1878 | 1017.5778
[5 empty] | 270 | 999.917 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 26.936 | 25.0432 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 26.936 | 1026.853 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 25.0432 | 1024.9602 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 21.9604 | 1021.8774 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 16.3655 | 1016.2825
[5 empty] | 272 | 1004.623 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 21.438 | 19.4551 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 21.438 | 1026.061 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 19.4551 | 1024.0781 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 16.2256 | 1020.8486 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 10.3642 | 1014.9872 | 1013.6919
|  |  |  | Reservoir | 274 | 1008.819 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 10 | 175 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 165 | 10 | 1183.819 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 165 | 175 | 1183.819 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 165 | 175 | 1183.819 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 165 | 175 | 1183.819 | 170.1271
[5 empty] | 276 | 1007.834 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 175.193 | 175.1029 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 175.193 | 1183.027 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 175.1029 | 1182.9369 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 174.9561 | 1182.7901 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 174.6897 | 1182.5237
[5 empty] | 278 | 1005.626 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 176.6091 | 176.4288 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 176.6091 | 1182.2351 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 176.4288 | 1182.0548 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 176.1352 | 1181.7612 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 175.6024 | 1181.2284
[5 empty] | 280 | 1001.623 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 179.8201 | 179.5497 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 179.8201 | 1181.4431 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 179.5497 | 1181.1727 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 179.1093 | 1180.7323 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 178.3101 | 1179.9331
[5 empty] | 282 | 1004.052 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 176.5992 | 176.2387 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 176.5992 | 1180.6512 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 176.2387 | 1180.2907 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 175.6515 | 1179.7035 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 174.5858 | 1178.6378
[5 empty] | 284 | 1010.797 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 169.0622 | 168.6116 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 169.0622 | 1179.8592 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 168.6116 | 1179.4086 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 167.8776 | 1178.6746 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 166.5455 | 1177.3425
[5 empty] | 286 | 1014.67 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 164.3973 | 163.8565 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 164.3973 | 1179.0673 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 163.8565 | 1178.5265 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 162.9757 | 1177.6457 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 161.3771 | 1176.0471
[5 empty] | 288 | 1017.319 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 160.9563 | 160.3254 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 160.9563 | 1178.2753 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 160.3254 | 1177.6444 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 159.2978 | 1176.6168 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 157.4328 | 1174.7518
[5 empty] | 290 | 1027.459 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 150.0244 | 149.3033 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 150.0244 | 1177.4834 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 149.3033 | 1176.7623 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 148.1289 | 1175.5879 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 145.9975 | 1173.4565
[5 empty] | 292 | 1031.99 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 144.7014 | 143.8902 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 144.7014 | 1176.6914 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 143.8902 | 1175.8802 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 142.569 | 1174.559 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 140.1712 | 1172.1612
[5 empty] | 294 | 1036.254 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 139.6455 | 138.7441 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 139.6455 | 1175.8995 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 138.7441 | 1174.9981 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 137.2762 | 1173.5302 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 134.6119 | 1170.8659
[5 empty] | 296 | 1040.127 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 134.9805 | 133.989 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 134.9805 | 1175.1075 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 133.989 | 1174.116 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 132.3743 | 1172.5013 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 129.4436 | 1169.5706
[5 empty] | 298 | 1044.396 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 129.9196 | 128.838 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 129.9196 | 1174.3156 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 128.838 | 1173.234 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 127.0764 | 1171.4724 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 123.8793 | 1168.2753
[5 empty] | 300 | 1051.339 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 122.1846 | 121.0129 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 122.1846 | 1173.5236 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 121.0129 | 1172.3519 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 119.1045 | 1170.4435 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 115.641 | 1166.98
[5 empty] | 302 | 1060.955 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 111.7767 | 110.5148 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 111.7767 | 1172.7317 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 110.5148 | 1171.4698 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 108.4596 | 1169.4146 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 104.7297 | 1165.6847
[5 empty] | 304 | 1070.227 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 101.7127 | 100.3607 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 101.7127 | 1171.9397 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 100.3607 | 1170.5877 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 98.1587 | 1168.3857 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 94.1624 | 1164.3894
[5 empty] | 306 | 1072.691 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 98.4568 | 97.0146 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 98.4568 | 1171.1478 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 97.0146 | 1169.7056 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 94.6659 | 1167.3569 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 90.403 | 1163.094
[5 empty] | 308 | 1076.503 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 93.8528 | 92.3205 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 93.8528 | 1170.3558 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 92.3205 | 1168.8235 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 89.825 | 1166.328 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 85.2957 | 1161.7987
[5 empty] | 310 | 1083.996 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 85.5679 | 83.9454 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 85.5679 | 1169.5639 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 83.9454 | 1167.9414 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 81.3031 | 1165.2991 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 76.5074 | 1160.5034
[5 empty] | 312 | 1097.188 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 71.5839 | 69.8714 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 71.5839 | 1168.7719 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 69.8714 | 1167.0594 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 67.0822 | 1164.2702 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 62.0201 | 1159.2081
[5 empty] | 314 | 1103.545 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 64.435 | 62.6323 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 64.435 | 1167.98 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 62.6323 | 1166.1773 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 59.6963 | 1163.2413 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 54.3678 | 1157.9128
[5 empty] | 316 | 1105.174 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 62.014 | 60.1212 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 62.014 | 1167.188 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 60.1212 | 1165.2952 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 57.0384 | 1162.2124 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 51.4435 | 1156.6175
[5 empty] | 318 | 1111.657 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 54.739 | 52.7561 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 54.739 | 1166.396 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 52.7561 | 1164.4131 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 49.5266 | 1161.1836 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 43.6652 | 1155.3222
[5 empty] | 320 | 1122.935 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 42.6691 | 40.596 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 42.6691 | 1165.6041 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 40.596 | 1163.531 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 37.2197 | 1160.1547 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 31.0919 | 1154.0269
[5 empty] | 322 | 1128.197 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 36.6151 | 34.4519 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 36.6151 | 1164.8121 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 34.4519 | 1162.6489 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 30.9288 | 1159.1258 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 24.5346 | 1152.7316
[5 empty] | 324 | 1132.561 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 31.4592 | 29.2058 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 31.4592 | 1164.0202 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 29.2058 | 1161.7668 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 25.5359 | 1158.0969 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 18.8753 | 1151.4363
[5 empty] | 326 | 1131.854 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 31.3742 | 29.0308 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 31.3742 | 1163.2282 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 29.0308 | 1160.8848 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 25.214 | 1157.068 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 18.2869 | 1150.1409
[5 empty] | 328 | 1133.338 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 29.0983 | 26.6647 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.051658 | 0.79195 | 0 | 29.0983 | 1162.4363 | 0.0096454 | 0.83043 | 0.051658 | 0.88209 | 0 | 26.6647 | 1160.0027 | 0.01135 | 0.97723 | 0.051658 | 1.0289 | 0 | 22.7011 | 1156.0391 | 0.014387 | 1.2437 | 0.051658 | 1.2953 | 0 | 15.5076 | 1148.8456
|  |  |  | Reservoir | 330 | 1136.405 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 10 | 10 | 10 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 10 | 1146.405 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 10 | 1146.405 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 10 | 1146.405 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 10 | 1146.405
[5 empty] | 332 | 1128.709 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 17.696 | 16.342 | 17.696 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 16.342 | 1145.051 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 16.1853 | 1144.8943 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 15.9296 | 1144.6386 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 15.463 | 1144.172
[5 empty] | 334 | 1120.713 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 25.692 | 22.984 | 25.692 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 22.984 | 1143.697 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 22.6706 | 1143.3836 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 22.1591 | 1142.8721 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 21.2259 | 1141.9389
[5 empty] | 336 | 1115.226 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 31.179 | 27.1171 | 31.179 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 27.1171 | 1142.3431 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 26.6469 | 1141.8729 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 25.8797 | 1141.1057 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 24.4799 | 1139.7059
[5 empty] | 338 | 1108.709 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 37.696 | 32.2801 | 37.696 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 32.2801 | 1140.9891 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 31.6532 | 1140.3622 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 30.6303 | 1139.3393 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 28.7638 | 1137.4728
[5 empty] | 340 | 1102.499 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 43.906 | 37.1361 | 43.906 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 37.1361 | 1139.6351 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 36.3525 | 1138.8515 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 35.0739 | 1137.5729 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 32.7408 | 1135.2398
[5 empty] | 342 | 1096.349 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 50.056 | 41.9321 | 50.056 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 41.9321 | 1138.2811 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 40.9918 | 1137.3408 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 39.4574 | 1135.8064 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 36.6577 | 1133.0067
[5 empty] | 344 | 1090.39 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 56.015 | 46.5371 | 56.015 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 46.5371 | 1136.9271 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 45.4401 | 1135.8301 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 43.65 | 1134.04 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 40.3837 | 1130.7737
[5 empty] | 346 | 1087.765 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 58.64 | 47.8081 | 58.64 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 47.8081 | 1135.5731 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 46.5544 | 1134.3194 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 44.5086 | 1132.2736 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 40.7756 | 1128.5406
[5 empty] | 348 | 1084.661 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 61.744 | 49.5582 | 61.744 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 49.5582 | 1134.2192 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 48.1477 | 1132.8087 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 45.8462 | 1130.5072 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 41.6466 | 1126.3076
[5 empty] | 350 | 1081.662 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 64.743 | 51.2032 | 64.743 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 51.2032 | 1132.8652 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 49.636 | 1131.298 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 47.0787 | 1128.7407 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 42.4126 | 1124.0746
[5 empty] | 352 | 1076.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 69.533 | 54.6392 | 69.533 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 54.6392 | 1131.5112 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 52.9153 | 1129.7873 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 50.1023 | 1126.9743 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 44.9695 | 1121.8415
[5 empty] | 354 | 1070.898 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 75.507 | 59.2592 | 75.507 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 59.2592 | 1130.1572 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 57.3786 | 1128.2766 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 54.3099 | 1125.2079 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 48.7105 | 1119.6085
[5 empty] | 356 | 1065.018 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 81.387 | 63.7852 | 81.387 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 63.7852 | 1128.8032 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 61.7479 | 1126.7659 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 58.4235 | 1123.4415 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 52.3574 | 1117.3754
[5 empty] | 358 | 1059.58 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 86.825 | 67.8693 | 86.825 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 67.8693 | 1127.4493 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 65.6752 | 1125.2552 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 62.095 | 1121.675 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.5624 | 1115.1424
[5 empty] | 360 | 1055.284 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 91.121 | 70.8113 | 91.121 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 70.8113 | 1126.0953 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 68.4605 | 1123.7445 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 64.6246 | 1119.9086 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 57.6253 | 1112.9093
[5 empty] | 362 | 1050.886 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 95.519 | 73.8553 | 95.519 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 73.8553 | 1124.7413 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 71.3478 | 1122.2338 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 67.2562 | 1118.1422 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 59.7903 | 1110.6763
[5 empty] | 364 | 1052.647 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 93.758 | 70.7403 | 93.758 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 70.7403 | 1123.3873 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 68.0761 | 1120.7231 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 63.7288 | 1116.3758 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.7962 | 1108.4432
[5 empty] | 366 | 1051.117 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 95.288 | 70.9163 | 95.288 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 70.9163 | 1122.0333 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 68.0954 | 1119.2124 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 63.4923 | 1114.6093 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.0932 | 1106.2102
[5 empty] | 368 | 1048.266 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 98.139 | 72.4133 | 98.139 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 72.4133 | 1120.6793 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 69.4357 | 1117.7017 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 64.5769 | 1112.8429 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.7112 | 1103.9772
[5 empty] | 370 | 1040.172 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 106.233 | 79.1534 | 106.233 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 79.1534 | 1119.3254 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 76.0191 | 1116.1911 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 70.9045 | 1111.0765 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 61.5721 | 1101.7441
[5 empty] | 372 | 1033.483 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 112.922 | 84.4884 | 112.922 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 84.4884 | 1117.9714 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 81.1974 | 1114.6804 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 75.8271 | 1109.3101 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 66.0281 | 1099.5111
[5 empty] | 374 | 1030.95 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 115.455 | 85.6674 | 115.455 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 85.6674 | 1116.6174 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 82.2197 | 1113.1697 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 76.5936 | 1107.5436 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 66.328 | 1097.278
[5 empty] | 376 | 1032.263 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 114.142 | 83.0004 | 114.142 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 83.0004 | 1115.2634 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.396 | 1111.659 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 73.5142 | 1105.7772 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 62.782 | 1095.045
[5 empty] | 378 | 1031.391 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 115.014 | 82.5184 | 115.014 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 82.5184 | 1113.9094 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 78.7573 | 1110.1483 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 72.6198 | 1104.0108 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 61.4209 | 1092.8119
[5 empty] | 380 | 1025.791 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 120.614 | 86.7645 | 120.614 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 86.7645 | 1112.5555 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 82.8466 | 1108.6376 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 76.4534 | 1102.2444 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 64.7879 | 1090.5789
[5 empty] | 382 | 1020.911 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 125.494 | 90.2905 | 125.494 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 90.2905 | 1111.2015 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 86.2159 | 1107.1269 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 79.5669 | 1100.4779 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 67.4348 | 1088.3458
[5 empty] | 384 | 1015.65 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 130.755 | 94.1975 | 130.755 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 94.1975 | 1109.8475 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 89.9662 | 1105.6162 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 83.0615 | 1098.7115 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 70.4628 | 1086.1128
[5 empty] | 386 | 1012.139 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 134.266 | 96.3545 | 134.266 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 96.3545 | 1108.4935 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 91.9665 | 1104.1055 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 84.8061 | 1096.9451 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 71.7407 | 1083.8797
[5 empty] | 388 | 1010.472 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 135.933 | 96.6675 | 135.933 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 96.6675 | 1107.1395 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 92.1228 | 1102.5948 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 84.7067 | 1095.1787 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 71.1747 | 1081.6467
[5 empty] | 390 | 1005.401 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 141.004 | 100.3845 | 141.004 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 100.3845 | 1105.7855 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 95.6831 | 1101.0841 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 88.0112 | 1093.4122 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 74.0127 | 1079.4137
[5 empty] | 392 | 996.666 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 149.739 | 107.7656 | 149.739 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 107.7656 | 1104.4316 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 102.9074 | 1099.5734 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 94.9798 | 1091.6458 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 80.5146 | 1077.1806
[5 empty] | 394 | 991.35 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 155.055 | 111.7276 | 155.055 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 111.7276 | 1103.0776 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 106.7127 | 1098.0627 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 98.5294 | 1089.8794 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 83.5976 | 1074.9476
[5 empty] | 396 | 990.486 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 155.919 | 111.2376 | 155.919 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 111.2376 | 1101.7236 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 106.066 | 1096.552 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 97.627 | 1088.113 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 82.2285 | 1072.7145
[5 empty] | 398 | 992.761 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 153.644 | 107.6086 | 153.644 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 107.6086 | 1100.3696 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 102.2803 | 1095.0413 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 93.5855 | 1086.3465 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 77.7205 | 1070.4815
[5 empty] | 400 | 999.077 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 147.328 | 99.9386 | 147.328 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 99.9386 | 1099.0156 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 94.4536 | 1093.5306 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 85.5031 | 1084.5801 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 69.1714 | 1068.2484
[5 empty] | 402 | 1001.8 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 144.605 | 95.8616 | 144.605 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 95.8616 | 1097.6616 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 90.2199 | 1092.0199 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 81.0137 | 1082.8137 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 64.2154 | 1066.0154
[5 empty] | 404 | 1002.224 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 144.181 | 94.0837 | 144.181 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 94.0837 | 1096.3077 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 88.2852 | 1090.5092 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 78.8233 | 1081.0473 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 61.5583 | 1063.7823
[5 empty] | 406 | 1002.003 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 144.402 | 92.9507 | 144.402 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.9507 | 1094.9537 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 86.9955 | 1088.9985 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 77.2778 | 1079.2808 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 59.5463 | 1061.5493
[5 empty] | 408 | 1003.596 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 142.809 | 90.0037 | 142.809 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 90.0037 | 1093.5997 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 83.8918 | 1087.4878 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 73.9184 | 1077.5144 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.7203 | 1059.3163
[5 empty] | 410 | 994.111 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 152.294 | 98.1347 | 152.294 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 98.1347 | 1092.2457 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 91.8661 | 1085.9771 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 81.637 | 1075.748 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 62.9722 | 1057.0832
[5 empty] | 412 | 983.925 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 162.48 | 106.9667 | 162.48 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 106.9667 | 1090.8917 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 100.5414 | 1084.4664 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 90.0566 | 1073.9816 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 70.9252 | 1054.8502
[5 empty] | 414 | 972.347 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 174.058 | 117.1908 | 174.058 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 117.1908 | 1089.5378 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 110.6087 | 1082.9557 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 99.8681 | 1072.2151 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 80.2701 | 1052.6171
[5 empty] | 416 | 963.901 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 182.504 | 124.2828 | 182.504 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 124.2828 | 1088.1838 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 117.544 | 1081.445 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 106.5477 | 1070.4487 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 86.4831 | 1050.3841
[5 empty] | 418 | 963.258 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.147 | 123.5718 | 183.147 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 123.5718 | 1086.8298 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 116.6763 | 1079.9343 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 105.4243 | 1068.6823 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 84.893 | 1048.151
[5 empty] | 420 | 965.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.533 | 119.6038 | 180.533 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 119.6038 | 1085.4758 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 112.5516 | 1078.4236 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 101.0439 | 1066.9159 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 80.046 | 1045.918
[5 empty] | 422 | 966.177 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.228 | 117.9448 | 180.228 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 117.9448 | 1084.1218 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 110.7359 | 1076.9129 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 98.9724 | 1065.1494 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 77.5079 | 1043.6849
[5 empty] | 424 | 973.825 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 172.58 | 108.9428 | 172.58 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 108.9428 | 1082.7678 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 101.5772 | 1075.4022 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 89.558 | 1063.383 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 67.6269 | 1041.4519
[5 empty] | 426 | 983.972 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 162.433 | 97.4419 | 162.433 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 97.4419 | 1081.4139 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 89.9195 | 1073.8915 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 77.6446 | 1061.6166 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.2469 | 1039.2189
[5 empty] | 428 | 994.096 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 152.309 | 85.9639 | 152.309 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 85.9639 | 1080.0599 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 78.2848 | 1072.3808 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 65.7542 | 1059.8502 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 42.8898 | 1036.9858
[5 empty] | 430 | 991.695 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 154.71 | 87.0109 | 154.71 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 87.0109 | 1078.7059 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 79.1751 | 1070.8701 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 66.3887 | 1058.0837 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 43.0578 | 1034.7528
[5 empty] | 432 | 984.933 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 161.472 | 92.4189 | 161.472 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 92.4189 | 1077.3519 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 84.4264 | 1069.3594 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 71.3843 | 1056.3173 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 47.5867 | 1032.5197
[5 empty] | 434 | 974.509 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 171.896 | 101.4889 | 171.896 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 101.4889 | 1075.9979 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 93.3397 | 1067.8487 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 80.0419 | 1054.5509 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 55.7777 | 1030.2867
[5 empty] | 436 | 966.698 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 179.707 | 107.946 | 179.707 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 107.946 | 1074.644 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 99.64 | 1066.338 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 86.0865 | 1052.7845 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 61.3556 | 1028.0536
[5 empty] | 438 | 963.618 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 182.787 | 109.672 | 182.787 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 109.672 | 1073.29 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 101.2093 | 1064.8273 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 87.4 | 1051.018 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 62.2026 | 1025.8206
[5 empty] | 440 | 957.803 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 188.602 | 114.133 | 188.602 | 11.3161 | 998345.0349 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 114.133 | 1071.936 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 105.5136 | 1063.3166 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 91.4486 | 1049.2516 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 65.7845 | 1023.5875
[5 empty] | 442 | 954.277 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 192.128 | 116.305 | 192.128 | 11.5277 | 1016889.2597 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 116.305 | 1070.582 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 107.5289 | 1061.8059 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 93.2082 | 1047.4852 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 67.0775 | 1021.3545
[5 empty] | 444 | 947.182 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 199.223 | 122.046 | 199.223 | 11.9534 | 1054190.4781 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 122.046 | 1069.228 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 113.1132 | 1060.2952 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 98.5368 | 1045.7188 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 71.9395 | 1019.1215
[5 empty] | 446 | 938.045 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 208.36 | 129.829 | 208.36 | 12.5016 | 1102200.9626 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 129.829 | 1067.874 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 120.7395 | 1058.7845 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 105.9073 | 1043.9523 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 78.8434 | 1016.8884
[5 empty] | 448 | 930.871 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 215.534 | 135.6491 | 215.534 | 12.932 | 1139876.0607 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 135.6491 | 1066.5201 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 126.4028 | 1057.2738 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 111.3149 | 1042.1859 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 83.7844 | 1014.6554
[5 empty] | 450 | 926.391 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 220.014 | 138.7751 | 220.014 | 13.2008 | 1163394.033 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 138.7751 | 1065.1661 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 129.3722 | 1055.7632 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 114.0285 | 1040.4195 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 86.0313 | 1012.4223
[5 empty] | 452 | 918.344 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 228.061 | 145.4681 | 228.061 | 13.6837 | 1205619.2415 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 145.4681 | 1063.8121 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 135.9085 | 1054.2525 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 120.3091 | 1038.6531 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 91.8453 | 1010.1893
[5 empty] | 454 | 911.505 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 234.9 | 150.9531 | 234.9 | 14.094 | 1241487.607 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 150.9531 | 1062.4581 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 141.2368 | 1052.7418 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 125.3816 | 1036.8866 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 96.4512 | 1007.9562
[5 empty] | 456 | 903.61 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 242.795 | 157.4941 | 242.795 | 14.5677 | 1282873.6994 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 157.4941 | 1061.1041 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 147.6211 | 1051.2311 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 131.5102 | 1035.1202 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 102.1132 | 1005.7232
[5 empty] | 458 | 900.63 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 245.775 | 159.1202 | 245.775 | 14.7465 | 1298489.2946 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 159.1202 | 1059.7502 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 149.0904 | 1049.7204 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 132.7238 | 1033.3538 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 102.8601 | 1003.4901
[5 empty] | 460 | 904.066 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 242.339 | 154.3302 | 242.339 | 14.5403 | 1280483.9207 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 154.3302 | 1058.3962 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 144.1437 | 1048.2097 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 127.5214 | 1031.5874 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 97.1911 | 1001.2571
[5 empty] | 462 | 915.092 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 231.313 | 141.9502 | 231.313 | 13.8788 | 1222677.0116 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 141.9502 | 1057.0422 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 131.607 | 1046.699 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 114.7289 | 1029.8209 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 83.932 | 999.024
[5 empty] | 464 | 905.556 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 240.849 | 150.1322 | 240.849 | 14.4509 | 1272674.6991 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 150.1322 | 1055.6882 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 139.6323 | 1045.1883 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 122.4985 | 1028.0545 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 91.235 | 996.791
[5 empty] | 466 | 905.271 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 241.134 | 149.0632 | 241.134 | 14.468 | 1274168.4703 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 149.0632 | 1054.3342 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 138.4066 | 1043.6776 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 121.0171 | 1026.2881 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 89.287 | 994.558
[5 empty] | 468 | 901.918 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 244.487 | 151.0622 | 244.487 | 14.6692 | 1291740.3907 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 151.0622 | 1052.9802 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 140.2489 | 1042.1669 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 122.6037 | 1024.5217 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 90.4069 | 992.3249
[5 empty] | 470 | 895.651 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 250.754 | 155.9753 | 250.754 | 15.0452 | 1324572.8786 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 155.9753 | 1051.6263 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 145.0052 | 1040.6562 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 127.1042 | 1022.7552 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 94.4409 | 990.0919
[5 empty] | 472 | 892.304 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 254.101 | 157.9683 | 254.101 | 15.2461 | 1342101.9243 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 157.9683 | 1050.2723 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 146.8415 | 1039.1455 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 128.6848 | 1020.9888 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 95.5548 | 987.8588
[5 empty] | 474 | 895.279 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 251.126 | 153.6393 | 251.126 | 15.0676 | 1326521.3288 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 153.6393 | 1048.9183 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 142.3558 | 1037.6348 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 123.9434 | 1019.2224 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 90.3468 | 985.6258
[5 empty] | 476 | 896.818 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 249.587 | 150.7463 | 249.587 | 14.9752 | 1318460.0829 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 150.7463 | 1047.5643 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 139.3061 | 1036.1241 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 120.638 | 1017.456 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 86.5747 | 983.3927
[5 empty] | 478 | 909.921 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 236.484 | 136.2893 | 236.484 | 14.189 | 1249792.8108 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 136.2893 | 1046.2103 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 124.6924 | 1034.6134 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 105.7685 | 1015.6895 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 71.2387 | 981.1597
[5 empty] | 480 | 926.295 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 220.11 | 118.5614 | 220.11 | 13.2066 | 1163897.9115 | 0.0087463 | 1.2752 | 0.078734 | 1.354 | 0 | 118.5614 | 1044.8564 | 0.0098211 | 1.432 | 0.078734 | 1.5107 | 0 | 106.8077 | 1033.1027 | 0.011575 | 1.6877 | 0.078734 | 1.7664 | 0 | 87.6281 | 1013.9231 | 0.01471 | 2.1543 | 0.078734 | 2.233 | 0 | 52.6316 | 978.9266
[5 empty] | 482 | 924.888 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 221.517 | 116.5357 | 221.517 | 11.0758 | 813390.6291 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 116.5357 | 1041.4237 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 104.3737 | 1029.2617 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 84.5255 | 1009.4135 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 48.2967 | 973.1847
[5 empty] | 484 | 919.044 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 227.361 | 118.9471 | 227.361 | 11.368 | 834685.4365 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 118.9471 | 1037.9911 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 106.3767 | 1025.4207 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 85.8599 | 1004.9039 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 48.3988 | 967.4428
[5 empty] | 486 | 911.164 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 235.241 | 123.3945 | 235.241 | 11.7621 | 863385.8389 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 123.3945 | 1034.5585 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 110.4158 | 1021.5798 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 89.2303 | 1000.3943 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 50.5368 | 961.7008
[5 empty] | 488 | 903.893 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 242.512 | 127.2329 | 242.512 | 12.1256 | 889854.568 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 127.2329 | 1031.1259 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 113.8458 | 1017.7388 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 91.9916 | 995.8846 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 52.0659 | 955.9589
[5 empty] | 490 | 901.953 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 244.452 | 125.7403 | 244.452 | 12.2226 | 896914.5753 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 125.7403 | 1027.6933 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 111.9448 | 1013.8978 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 89.422 | 991.375 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 48.264 | 950.217
[5 empty] | 492 | 900.198 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 246.207 | 124.0627 | 246.207 | 12.3103 | 903300.5349 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 124.0627 | 1024.2607 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 109.8588 | 1010.0568 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 86.6674 | 986.8654 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 44.277 | 944.475
[5 empty] | 494 | 904.177 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 242.228 | 116.6511 | 242.228 | 12.1114 | 888820.9632 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 116.6511 | 1020.8281 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 102.0389 | 1006.2159 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 78.1788 | 982.3558 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 34.5561 | 938.7331
[5 empty] | 496 | 912.253 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 234.152 | 105.1425 | 234.152 | 11.7076 | 859420.4135 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 105.1425 | 1017.3955 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 90.1219 | 1002.3749 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 65.5932 | 977.8462 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 20.7382 | 932.9912
[5 empty] | 498 | 915.297 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 231.108 | 98.6659 | 231.108 | 11.5554 | 848334.606 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 98.6659 | 1013.9629 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 83.2369 | 998.5339 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 58.0395 | 973.3365 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 11.9522 | 927.2492
|  |  |  | Reservoir | 500 | 919.629 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 10 | 226.776 | 10 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.16326 | 3.4326 | 0 | 226.776 | 929.629 | 0.010137 | 3.6777 | 0.16326 | 3.841 | 0 | 10 | 929.629 | 0.01198 | 4.3464 | 0.16326 | 4.5096 | 0 | 10 | 929.629 | 0.015294 | 5.5787 | 0.16326 | 5.7419 | 0 | 10 | 929.629
[15 empty] | Total Steel Mass (kg): | 272135556.4993