## Summary
Option 6A Summary
Item | Chainage | Value
Pipeline | 0-8 | 1.9 | m - Diameter
Pump Station | 8 | 50 | m - Pumping Head
Pipeline | 8-22 | 1.9 | m - Diameter
Break Pressure | 22 | 10 | m -Elevation
Pipeline | 22-164 | 1.9 | m - Diameter
Pipeline | 164-226 | 1.8 | m - Diameter
Pipeline | 226-228 | 2 | m - Diameter
Break Pressure | 228 | 10 | m - Elevation
Pump Station | 228 | 120 | m - Pumping Head
Pipeline | 228-274 | 2 | m -Diameter
Pump Station | 274 | 160 | m - Pumping Head
Pipeline | 274-330 | 2 | m -Diameter
Break Pressure | 330 | 10 | m - Elevation
Pipeline | 330-508 | 1.8 | m -Diameter
Pipeline | 508-520 | 1.5 | m -Diameter

## Control Points
Longitudinal profile data - Botswana pipeline
| OPTION 1: Pipeline goes through Serule before joining to BPT1 | OPTION2: Pipeline goes directly to BPT1
CHAINAGE (km0 | NGL (m) | NGL (m) |  | Botswana 1
2 | 1069.018 | 1069.018 | Start | Botswana 2
4 | 1067.321 | 1067.321
6 | 1064.035 | 1064.035
8 | 1063.832 | 1063.832
10 | 1067.893 | 1067.893
12 | 1075.133 | 1075.133
14 | 1082.768 | 1082.768
16 | 1089.726 | 1089.726
18 | 1094.131 | 1094.131
20 | 1097.897 | 1097.897
22 | 1101.67 | 1101.67
24 | 1095.952 | 1095.952
26 | 1090.107 | 1090.107
28 | 1085.781 | 1085.781
30 | 1081.89 | 1081.89
32 | 1077.937 | 1077.937
34 | 1074.89 | 1074.89
36 | 1071.114 | 1071.114
38 | 1065.311 | 1065.311
40 | 1059.051 | 1059.051
42 | 1054.28 | 1054.28
44 | 1053.871 | 1053.871
46 | 1050.42 | 1050.42
48 | 1052.704 | 1052.704
50 | 1056.355 | 1056.355
52 | 1058.466 | 1058.466
54 | 1055.99 | 1055.99
56 | 1055.66 | 1055.66
58 | 1056.404 | 1056.404
60 | 1056.841 | 1056.841
62 | 1056.377 | 1056.377
64 | 1052.503 | 1052.503
66 | 1046.022 | 1046.022
68 | 1036.575 | 1036.575
70 | 1031.818 | 1031.818
72 | 1027.675 | 1027.675
74 | 1023.844 | 1023.844
76 | 1020.888 | 1020.888
78 | 1023.648 | 1023.648
80 | 1027.566 | 1027.566
82 | 1032.371 | 1032.371
84 | 1034.983 | 1034.983
86 | 1033.213 | 1033.213
88 | 1031.188 | 1031.188
90 | 1029.08 | 1029.08
92 | 1026.322 | 1026.322
94 | 1023.207 | 1023.207
96 | 1021.503 | 1021.503
98 | 1019.765 | 1019.765
100 | 1018.493 | 1018.493
102 | 1016.444 | 1016.444
104 | 1013.288 | 1013.288
106 | 1007.843 | 1007.843
108 | 1001.282 | 1001.282
110 | 996.609 | 996.609
112 | 992.999 | 992.999
114 | 993.639 | 993.639
116 | 994.611 | 994.611
118 | 995.751 | 995.751
120 | 996.479 | 996.479
122 | 996.147 | 996.147
124 | 992.094 | 992.094
126 | 985.623 | 985.623
128 | 977.759 | 977.759
130 | 969.772 | 969.772
132 | 981.785 | 981.785
134 | 991.458 | 991.458
136 | 987.77 | 987.77
138 | 982.725 | 982.725
140 | 977.559 | 977.559
142 | 975.289 | 975.289
144 | 973.968 | 973.968
146 | 962.473 | 962.473
148 | 951.285 | 951.285
150 | 948.174 | 948.174
152 | 944.641 | 944.641
154 | 941.566 | 941.566
156 | 940.942 | 940.942
158 | 939.726 | 939.726
160 | 936.738 | 936.738
162 | 933.65 | 933.65
164 | 932.745 | 932.745
166 | 931.696 | 931.696
168 | 930.999 | 930.999
170 | 930.885 | 930.885
172 | 930.378 | 930.378
174 | 931.324 | 931.324
176 | 933.53 | 933.53
178 | 932.714 | 932.714
180 | 928.311 | 928.311
182 | 924.179 | 924.179
184 | 928.398 | 928.398
186 | 930.866 | 930.866
188 | 928.411 | 928.411
190 | 927.849 | 927.849
192 | 926.71 | 926.71
194 | 926.201 | 926.201
196 | 924.509 | 924.509
198 | 923.417 | 923.417
200 | 923.011 | 923.011
202 | 921.969 | 921.969
204 | 920.661 | 920.661
206 | 920.243 | 920.243
208 | 919.297 | 919.297
210 | 917.533 | 917.533
212 | 917.684 | 917.684
214 | 915.724 | 915.724
216 | 915.73 | 915.73
218 | 915.584 | 915.584
220 | 915.444 | 915.444
222 | 913.52 | 913.52
224 | 912.524 | 912.524
226 | 912.565 | 912.565
228 | 913.484 | 913.484
230 | 913.545 | 913.545
232 | 914.546 | 914.546
234 | 918.285 | 918.285
236 | 919.357 | 919.357
238 | 918.649 | 918.649
240 | 922.974 | 922.974
242 | 927.375 | 927.375
244 | 929.253 | 929.253
246 | 930.863 | 930.863
248 | 931.924 | 931.924
250 | 936.722 | 936.722
252 | 941.777 | 941.777
254 | 948.143 | 948.143
256 | 955.417 | 955.417
258 | 962.7 | 962.7
260 | 969.281 | 969.281
262 | 980.284 | 980.284
264 | 986.551 | 986.551
266 | 989.198 | 989.198
268 | 994.39 | 994.39
270 | 999.917 | 999.917
272 | 1004.623 | 1004.623
274 | 1008.819 | 1008.819
276 | 1007.834 | 1007.834
278 | 1005.626 | 1005.626
280 | 1001.623 | 1001.623
282 | 1004.052 | 1004.052
284 | 1010.797 | 1010.797
286 | 1014.67 | 1014.67
288 | 1017.319 | 1017.319
290 | 1027.459 | 1027.459
292 | 1031.99 | 1031.99
294 | 1036.254 | 1036.254
296 | 1040.127 | 1040.127
298 | 1044.396 | 1044.396
300 | 1051.339 | 1051.339
302 | 1060.955 | 1060.955
304 | 1070.227 | 1070.227
306 | 1072.691 | 1072.691
308 | 1076.503 | 1076.503
310 | 1083.996 | 1083.996
312 | 1097.188 | 1097.188
314 | 1103.545 | 1103.545
316 | 1105.174 | 1105.174
318 | 1111.657 | 1111.657
320 | 1122.935 | 1122.935
322 | 1128.197 | 1128.197
324 | 1132.561 | 1132.561
326 | 1131.854 | 1131.854
328 | 1133.338 | 1133.338
330 | 1136.405 | 1136.405
332 | 1128.709 | 1128.709
334 | 1120.713 | 1120.713
336 | 1115.226 | 1115.226
338 | 1108.709 | 1108.709
340 | 1102.499 | 1102.499
342 | 1096.349 | 1096.349
344 | 1090.39 | 1090.39
346 | 1087.765 | 1087.765
348 | 1084.661 | 1084.661
350 | 1081.662 | 1081.662
352 | 1076.872 | 1076.872
354 | 1070.898 | 1070.898
356 | 1065.018 | 1065.018
358 | 1059.58 | 1059.58
360 | 1055.284 | 1055.284
362 | 1050.886 | 1050.886
364 | 1052.647 | 1052.647
366 | 1051.117 | 1051.117
368 | 1048.266 | 1048.266
370 | 1040.172 | 1040.172
372 | 1033.483 | 1033.483
374 | 1030.95 | 1030.95
376 | 1032.263 | 1032.263
378 | 1031.391 | 1031.391
380 | 1025.791 | 1025.791
382 | 1020.911 | 1020.911
384 | 1015.65 | 1015.65
386 | 1012.139 | 1012.139
388 | 1010.472 | 1010.472
390 | 1005.401 | 1005.401
392 | 996.666 | 996.666
394 | 991.35 | 991.35
396 | 990.486 | 990.486
398 | 992.761 | 992.761
400 | 999.077 | 999.077
402 | 1001.8 | 1001.8
404 | 1002.224 | 1002.224
406 | 1002.003 | 1002.003
408 | 1003.596 | 1003.596
410 | 994.111 | 994.111
412 | 983.925 | 983.925
414 | 972.347 | 972.347
416 | 963.901 | 963.901
418 | 963.258 | 963.258
420 | 965.836 | 965.872
422 | 966.309 | 966.177
424 | 972.884 | 973.825
426 | 983.972 | 983.972
428 | 994.096 | 994.096
430 | 991.695 | 991.695
432 | 984.933 | 984.933
434 | 978.185 | 974.509
436 | 972.686 | 966.698
438 | 966.824 | 963.618
440 | 960.902 | 957.803
442 | 952.924 | 954.277
444 | 945.683 | 947.182
446 | 941.042 | 938.045
448 | 937.104 | 930.871
450 | 939.943 | 926.391
452 | 944.776 | 918.344
454 | 947.762 | 911.505
456 | 952.649 | 903.61
458 | 954.554 | 900.63
460 | 952.37 | 904.066
462 | 947.552 | 915.092
464 | 941.898 | 905.556
466 | 940.521 | 905.271
468 | 939.702 | 901.918
470 | 937.147 | 895.651
472 | 933.872 | 892.304
474 | 933.184 | 895.279
476 | 939.292 | 896.818
478 | 944.619 | 909.921
480 | 954.023 | 926.295
482 | 968.263 | 924.888
484 | 970.384 | 919.044
486 | 964.636 | 911.164
488 | 956.631 | 903.893
490 | 947.426 | 901.953
492 | 941.72 | 900.198
494 | 935.985 | 904.177
496 | 930.475 | 912.253
498 | 927.611 | 915.297
500 | 931.256 | 919.629
502 | 920.044
504 | 911.78
506 | 907.989
508 | 907.289
510 | 900.577
512 | 902.112
514 | 900.179
516 | 903.811
518 | 910.027
520 | 911.131 |  | End

## Profile data
Longitudinal profile data - Botswana pipeline
| OPTION 1: Pipeline goes through Serule before joining to BPT1 | OPTION2: Pipeline goes directly to BPT1
CHAINAGE (km0 | NGL (m) | NGL (m) |  | Botswana 1
2 | 1069.018 | 1069.018 | Start | Botswana 2
4 | 1067.321 | 1067.321
6 | 1064.035 | 1064.035
8 | 1063.832 | 1063.832
10 | 1067.893 | 1067.893
12 | 1075.133 | 1075.133
14 | 1082.768 | 1082.768
16 | 1089.726 | 1089.726
18 | 1094.131 | 1094.131
20 | 1097.897 | 1097.897
22 | 1101.67 | 1101.67
24 | 1095.952 | 1095.952
26 | 1090.107 | 1090.107
28 | 1085.781 | 1085.781
30 | 1081.89 | 1081.89
32 | 1077.937 | 1077.937
34 | 1074.89 | 1074.89
36 | 1071.114 | 1071.114
38 | 1065.311 | 1065.311
40 | 1059.051 | 1059.051
42 | 1054.28 | 1054.28
44 | 1053.871 | 1053.871
46 | 1050.42 | 1050.42
48 | 1052.704 | 1052.704
50 | 1056.355 | 1056.355
52 | 1058.466 | 1058.466
54 | 1055.99 | 1055.99
56 | 1055.66 | 1055.66
58 | 1056.404 | 1056.404
60 | 1056.841 | 1056.841
62 | 1056.377 | 1056.377
64 | 1052.503 | 1052.503
66 | 1046.022 | 1046.022
68 | 1036.575 | 1036.575
70 | 1031.818 | 1031.818
72 | 1027.675 | 1027.675
74 | 1023.844 | 1023.844
76 | 1020.888 | 1020.888
78 | 1023.648 | 1023.648
80 | 1027.566 | 1027.566
82 | 1032.371 | 1032.371
84 | 1034.983 | 1034.983
86 | 1033.213 | 1033.213
88 | 1031.188 | 1031.188
90 | 1029.08 | 1029.08
92 | 1026.322 | 1026.322
94 | 1023.207 | 1023.207
96 | 1021.503 | 1021.503
98 | 1019.765 | 1019.765
100 | 1018.493 | 1018.493
102 | 1016.444 | 1016.444
104 | 1013.288 | 1013.288
106 | 1007.843 | 1007.843
108 | 1001.282 | 1001.282
110 | 996.609 | 996.609
112 | 992.999 | 992.999
114 | 993.639 | 993.639
116 | 994.611 | 994.611
118 | 995.751 | 995.751
120 | 996.479 | 996.479
122 | 996.147 | 996.147
124 | 992.094 | 992.094
126 | 985.623 | 985.623
128 | 977.759 | 977.759
130 | 969.772 | 969.772
132 | 981.785 | 981.785
134 | 991.458 | 991.458
136 | 987.77 | 987.77
138 | 982.725 | 982.725
140 | 977.559 | 977.559
142 | 975.289 | 975.289
144 | 973.968 | 973.968
146 | 962.473 | 962.473
148 | 951.285 | 951.285
150 | 948.174 | 948.174
152 | 944.641 | 944.641
154 | 941.566 | 941.566
156 | 940.942 | 940.942
158 | 939.726 | 939.726
160 | 936.738 | 936.738
162 | 933.65 | 933.65
164 | 932.745 | 932.745
166 | 931.696 | 931.696
168 | 930.999 | 930.999
170 | 930.885 | 930.885
172 | 930.378 | 930.378
174 | 931.324 | 931.324
176 | 933.53 | 933.53
178 | 932.714 | 932.714
180 | 928.311 | 928.311
182 | 924.179 | 924.179
184 | 928.398 | 928.398
186 | 930.866 | 930.866
188 | 928.411 | 928.411
190 | 927.849 | 927.849
192 | 926.71 | 926.71
194 | 926.201 | 926.201
196 | 924.509 | 924.509
198 | 923.417 | 923.417
200 | 923.011 | 923.011
202 | 921.969 | 921.969
204 | 920.661 | 920.661
206 | 920.243 | 920.243
208 | 919.297 | 919.297
210 | 917.533 | 917.533
212 | 917.684 | 917.684
214 | 915.724 | 915.724
216 | 915.73 | 915.73
218 | 915.584 | 915.584
220 | 915.444 | 915.444
222 | 913.52 | 913.52
224 | 912.524 | 912.524
226 | 912.565 | 912.565
228 | 913.484 | 913.484
230 | 913.545 | 913.545
232 | 914.546 | 914.546
234 | 918.285 | 918.285
236 | 919.357 | 919.357
238 | 918.649 | 918.649
240 | 922.974 | 922.974
242 | 927.375 | 927.375
244 | 929.253 | 929.253
246 | 930.863 | 930.863
248 | 931.924 | 931.924
250 | 936.722 | 936.722
252 | 941.777 | 941.777
254 | 948.143 | 948.143
256 | 955.417 | 955.417
258 | 962.7 | 962.7
260 | 969.281 | 969.281
262 | 980.284 | 980.284
264 | 986.551 | 986.551
266 | 989.198 | 989.198
268 | 994.39 | 994.39
270 | 999.917 | 999.917
272 | 1004.623 | 1004.623
274 | 1008.819 | 1008.819
276 | 1007.834 | 1007.834
278 | 1005.626 | 1005.626
280 | 1001.623 | 1001.623
282 | 1004.052 | 1004.052
284 | 1010.797 | 1010.797
286 | 1014.67 | 1014.67
288 | 1017.319 | 1017.319
290 | 1027.459 | 1027.459
292 | 1031.99 | 1031.99
294 | 1036.254 | 1036.254
296 | 1040.127 | 1040.127
298 | 1044.396 | 1044.396
300 | 1051.339 | 1051.339
302 | 1060.955 | 1060.955
304 | 1070.227 | 1070.227
306 | 1072.691 | 1072.691
308 | 1076.503 | 1076.503
310 | 1083.996 | 1083.996
312 | 1097.188 | 1097.188
314 | 1103.545 | 1103.545
316 | 1105.174 | 1105.174
318 | 1111.657 | 1111.657
320 | 1122.935 | 1122.935
322 | 1128.197 | 1128.197
324 | 1132.561 | 1132.561
326 | 1131.854 | 1131.854
328 | 1133.338 | 1133.338
330 | 1136.405 | 1136.405
332 | 1128.709 | 1128.709
334 | 1120.713 | 1120.713
336 | 1115.226 | 1115.226
338 | 1108.709 | 1108.709
340 | 1102.499 | 1102.499
342 | 1096.349 | 1096.349
344 | 1090.39 | 1090.39
346 | 1087.765 | 1087.765
348 | 1084.661 | 1084.661
350 | 1081.662 | 1081.662
352 | 1076.872 | 1076.872
354 | 1070.898 | 1070.898
356 | 1065.018 | 1065.018
358 | 1059.58 | 1059.58
360 | 1055.284 | 1055.284
362 | 1050.886 | 1050.886
364 | 1052.647 | 1052.647
366 | 1051.117 | 1051.117
368 | 1048.266 | 1048.266
370 | 1040.172 | 1040.172
372 | 1033.483 | 1033.483
374 | 1030.95 | 1030.95
376 | 1032.263 | 1032.263
378 | 1031.391 | 1031.391
380 | 1025.791 | 1025.791
382 | 1020.911 | 1020.911
384 | 1015.65 | 1015.65
386 | 1012.139 | 1012.139
388 | 1010.472 | 1010.472
390 | 1005.401 | 1005.401
392 | 996.666 | 996.666
394 | 991.35 | 991.35
396 | 990.486 | 990.486
398 | 992.761 | 992.761
400 | 999.077 | 999.077
402 | 1001.8 | 1001.8
404 | 1002.224 | 1002.224
406 | 1002.003 | 1002.003
408 | 1003.596 | 1003.596
410 | 994.111 | 994.111
412 | 983.925 | 983.925
414 | 972.347 | 972.347
416 | 963.901 | 963.901
418 | 963.258 | 963.258
420 | 965.836 | 965.872
422 | 966.309 | 966.177
424 | 972.884 | 973.825
426 | 983.972 | 983.972
428 | 994.096 | 994.096
430 | 991.695 | 991.695
432 | 984.933 | 984.933
434 | 978.185 | 974.509
436 | 972.686 | 966.698
438 | 966.824 | 963.618
440 | 960.902 | 957.803
442 | 952.924 | 954.277
444 | 945.683 | 947.182
446 | 941.042 | 938.045
448 | 937.104 | 930.871
450 | 939.943 | 926.391
452 | 944.776 | 918.344
454 | 947.762 | 911.505
456 | 952.649 | 903.61
458 | 954.554 | 900.63
460 | 952.37 | 904.066
462 | 947.552 | 915.092
464 | 941.898 | 905.556
466 | 940.521 | 905.271
468 | 939.702 | 901.918
470 | 937.147 | 895.651
472 | 933.872 | 892.304
474 | 933.184 | 895.279
476 | 939.292 | 896.818
478 | 944.619 | 909.921
480 | 954.023 | 926.295
482 | 968.263 | 924.888
484 | 970.384 | 919.044
486 | 964.636 | 911.164
488 | 956.631 | 903.893
490 | 947.426 | 901.953
492 | 941.72 | 900.198
494 | 935.985 | 904.177
496 | 930.475 | 912.253
498 | 927.611 | 915.297
500 | 931.256 | 919.629
502 | 920.044
504 | 911.78
506 | 907.989
508 | 907.289
510 | 900.577
512 | 902.112
514 | 900.179
516 | 903.811
518 | 910.027
520 | 911.131 |  | End

## Flow Rate Calculations
Estimated Transfer Rate Demand | 100 | Mm3/a
Availible Days | 365
Pumping Hours | 24
Pf | 1.052
Pl | 1.02
PR | 1.2
Peak Design Flow | 4.0831 | m3/s

## Calculation Constants
Friction Factors
Ks (mm) - New | 0.03
Ks (mm) - Average | 0.06
Ks (mm) - Old | 0.15
Ks (mm) - Biofilm | 0.5
Kinemeatic Viscosity | 1.13e-06 | m2/s
Minor Loss - k | 150
Grade of Steel | X42
Yeild Capacity | 300 | Mpa
Design % of Yeild | 50%
Minimum D/t ratio | 160 | mm/mm

## Hydraulics
Option 6A |  |  |  | Option 6A | [12 empty] | Option 6A
Pump Station |  |  |  | Pipe Line | [9 empty] | Steel Pipeline Design |  |  | New Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Average Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Old Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Biofilm Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes
Name | Chainage (km) | Elevation (m) | Pumped Head (m) | Reference | Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Flow Rate (m3/s) | PipeVelocity (m/s) | Re | Static Head (m) | Dynamic Head (m) | Design Pressure (m) | Pipe Wall thickness (mm) | Steel Mass (kg) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m)
PS 1 | 8 | 1063.832 | 50 | Reservoir | 2 | 1069.018 | 0 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 10 | 10 | 10 | 11.875 | 0 | 0.00867 |  |  | 0 | 0 | 10 | 1079.018 | 0.0097304 |  |  | 0 | 0 | 10 | 1079.018 | 0.011459 |  |  | 0 | 0 | 10 | 1079.018 | 0.014543 |  |  | 0 | 0 | 10 | 1079.018
PS 3 | 228 | 913.484 | 120 |  | 4 | 1067.321 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 11.697 | 10.6713 | 11.697 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 10.6713 | 1077.9923 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 10.5534 | 1077.8744 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 10.361 | 1077.682 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 10.011 | 1077.332
PS 2 | 274 | 1008.819 | 160 |  | 6 | 1064.035 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 14.983 | 12.9317 | 14.983 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 12.9317 | 1076.9667 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 12.6957 | 1076.7307 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 12.311 | 1076.346 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 11.6111 | 1075.6461
|  |  |  | Pump Station | 8 | 1063.832 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 62.109 | 61.7551 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 50 | 62.109 | 1125.941 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 50 | 61.7551 | 1125.5871 | 0.011459 | 1.275 | 0.060983 | 1.336 | 50 | 61.1781 | 1125.0101 | 0.014543 | 1.625 | 0.060983 | 1.686 | 50 | 60.1281 | 1123.9601
[5 empty] | 10 | 1067.893 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 57.0224 | 56.5504 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 57.0224 | 1124.9154 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 56.5504 | 1124.4434 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 55.7811 | 1123.6741 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 54.3812 | 1122.2742
Reservoirs |  |  |  |  | 12 | 1075.133 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 48.7567 | 48.1668 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 48.7567 | 1123.8897 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 48.1668 | 1123.2998 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 47.2051 | 1122.3381 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 45.4552 | 1120.5882
Name | Chainage (km) | Water Elevation (m) | Height |  | 14 | 1082.768 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 40.096 | 39.3881 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 40.096 | 1122.864 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 39.3881 | 1122.1561 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 38.2341 | 1121.0021 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 36.1343 | 1118.9023
Supply Resrvoir | 2 | 1079.018 | 10 |  | 16 | 1089.726 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 32.1124 | 31.2865 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 32.1124 | 1121.8384 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 31.2865 | 1121.0125 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 29.9401 | 1119.6661 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.4903 | 1117.2163
BPT 3 | 22 | 1111.67 | 10 |  | 18 | 1094.131 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 26.6817 | 25.7378 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 26.6817 | 1120.8127 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 25.7378 | 1119.8688 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 24.1991 | 1118.3301 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 21.3994 | 1115.5304
BPT 5 | 228 | 923.484 | 10 |  | 20 | 1097.897 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | Greater Dynamic Pressures | 21.8901 | 20.8282 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 21.8901 | 1119.7871 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 20.8282 | 1118.7252 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 19.0972 | 1116.9942 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 15.9474 | 1113.8444
BPT 4 | 274 | 1018.819 | 10 | Reservoir | 22 | 1101.67 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 10 | 10 | 10 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 10 | 1111.67 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 10 | 1111.67 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 10 | 1111.67 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 10 | 1111.67
BPT 2 | 330 | 1146.405 | 10 |  | 24 | 1095.952 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 15.718 | 14.6923 | 15.718 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 14.6923 | 1110.6443 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 14.5744 | 1110.5264 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 14.382 | 1110.334 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 14.032 | 1109.984
BPT 1 | 520 | 921.131 | 10 |  | 26 | 1090.107 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 21.563 | 19.5117 | 21.563 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 19.5117 | 1109.6187 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 19.2757 | 1109.3827 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 18.891 | 1108.998 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 18.1911 | 1108.2981
[5 empty] | 28 | 1085.781 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 25.889 | 22.812 | 25.889 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 22.812 | 1108.593 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 22.4581 | 1108.2391 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 21.8811 | 1107.6621 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 20.8311 | 1106.6121
|  | -95.335 |  |  | 30 | 1081.89 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 29.78 | 25.6774 | 29.78 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 25.6774 | 1107.5674 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 25.2054 | 1107.0954 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 24.4361 | 1106.3261 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 23.0362 | 1104.9262
[5 empty] | 32 | 1077.937 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 33.733 | 28.6047 | 33.733 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 28.6047 | 1106.5417 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 28.0148 | 1105.9518 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 27.0531 | 1104.9901 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 25.3032 | 1103.2402
[5 empty] | 34 | 1074.89 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 36.78 | 30.626 | 36.78 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 30.626 | 1105.516 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 29.9181 | 1104.8081 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 28.7641 | 1103.6541 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 26.6643 | 1101.5543
[5 empty] | 36 | 1071.114 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 40.556 | 33.3764 | 40.556 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 33.3764 | 1104.4904 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 32.5505 | 1103.6645 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 31.2041 | 1102.3181 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 28.7543 | 1099.8683
Route | Botswana 1 |  |  |  | 38 | 1065.311 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 46.359 | 38.1537 | 46.359 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 38.1537 | 1103.4647 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 37.2098 | 1102.5208 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 35.6711 | 1100.9821 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 32.8714 | 1098.1824
Option | 6A |  |  |  | 40 | 1059.051 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 52.619 | 43.3881 | 52.619 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 43.3881 | 1102.4391 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 42.3262 | 1101.3772 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 40.5952 | 1099.6462 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 37.4454 | 1096.4964
[5 empty] | 42 | 1054.28 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 57.39 | 47.1334 | 57.39 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 47.1334 | 1101.4134 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 45.9535 | 1100.2335 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 44.0302 | 1098.3102 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 40.5304 | 1094.8104
[5 empty] | 44 | 1053.871 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 57.799 | 46.5167 | 57.799 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 46.5167 | 1100.3877 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 45.2189 | 1099.0899 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 43.1032 | 1096.9742 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 39.2535 | 1093.1245
[5 empty] | 46 | 1050.42 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 61.25 | 48.9421 | 61.25 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 48.9421 | 1099.3621 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 47.5263 | 1097.9463 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 45.2182 | 1095.6382 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 41.0185 | 1091.4385
[5 empty] | 48 | 1052.704 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 58.966 | 45.6324 | 58.966 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 45.6324 | 1098.3364 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 44.0986 | 1096.8026 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 41.5982 | 1094.3022 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 37.0486 | 1089.7526
[5 empty] | 50 | 1056.355 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.315 | 40.9557 | 55.315 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 40.9557 | 1097.3107 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 39.304 | 1095.659 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 36.6113 | 1092.9663 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 31.7116 | 1088.0666
[5 empty] | 52 | 1058.466 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 53.204 | 37.8191 | 53.204 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 37.8191 | 1096.2851 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 36.0493 | 1094.5153 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 33.1643 | 1091.6303 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.9147 | 1086.3807
[5 empty] | 54 | 1055.99 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.68 | 39.2694 | 55.68 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 39.2694 | 1095.2594 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 37.3817 | 1093.3717 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 34.3043 | 1090.2943 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 28.7047 | 1084.6947
[5 empty] | 56 | 1055.66 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 56.01 | 38.5738 | 56.01 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 38.5738 | 1094.2338 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 36.568 | 1092.228 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 33.2983 | 1088.9583 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.3488 | 1083.0088
[5 empty] | 58 | 1056.404 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.266 | 36.8041 | 55.266 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 36.8041 | 1093.2081 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 34.6804 | 1091.0844 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 31.2183 | 1087.6223 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 24.9188 | 1081.3228
[5 empty] | 60 | 1056.841 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 54.829 | 35.3414 | 54.829 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 35.3414 | 1092.1824 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 33.0997 | 1089.9407 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 29.4453 | 1086.2863 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 22.7958 | 1079.6368
[5 empty] | 62 | 1056.377 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 55.293 | 34.7798 | 55.293 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 34.7798 | 1091.1568 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 32.4201 | 1088.7971 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 28.5734 | 1084.9504 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 21.5739 | 1077.9509
[5 empty] | 64 | 1052.503 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 59.167 | 37.6281 | 59.167 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 37.6281 | 1090.1311 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 35.1504 | 1087.6534 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 31.1114 | 1083.6144 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 23.7619 | 1076.2649
[5 empty] | 66 | 1046.022 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 65.648 | 43.0835 | 65.648 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 43.0835 | 1089.1055 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 40.4878 | 1086.5098 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 36.2564 | 1082.2784 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 28.557 | 1074.579
[5 empty] | 68 | 1036.575 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 75.095 | 51.5048 | 75.095 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 51.5048 | 1088.0798 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 48.7911 | 1085.3661 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 44.3674 | 1080.9424 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 36.318 | 1072.893
[5 empty] | 70 | 1031.818 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 79.852 | 55.2361 | 79.852 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 55.2361 | 1087.0541 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 52.4045 | 1084.2225 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 47.7884 | 1079.6064 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 39.3891 | 1071.2071
[5 empty] | 72 | 1027.675 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 83.995 | 58.3535 | 83.995 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 58.3535 | 1086.0285 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 55.4039 | 1083.0789 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 50.5955 | 1078.2705 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 41.8461 | 1069.5211
[5 empty] | 74 | 1023.844 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 87.826 | 61.1588 | 87.826 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 61.1588 | 1085.0028 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 58.0912 | 1081.9352 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 53.0905 | 1076.9345 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 43.9912 | 1067.8352
[5 empty] | 76 | 1020.888 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 90.782 | 63.0892 | 90.782 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 63.0892 | 1083.9772 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 59.9036 | 1080.7916 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 54.7105 | 1075.5985 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 45.2612 | 1066.1492
[5 empty] | 78 | 1023.648 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 88.022 | 59.3035 | 88.022 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 59.3035 | 1082.9515 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 55.9999 | 1079.6479 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 50.6145 | 1074.2625 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 40.8152 | 1064.4632
[5 empty] | 80 | 1027.566 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 84.104 | 54.3598 | 84.104 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 54.3598 | 1081.9258 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 50.9383 | 1078.5043 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 45.3605 | 1072.9265 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 35.2113 | 1062.7773
[5 empty] | 82 | 1032.371 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 79.299 | 48.5292 | 79.299 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 48.5292 | 1080.9002 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 44.9896 | 1077.3606 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 39.2195 | 1071.5905 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 28.7203 | 1061.0913
[5 empty] | 84 | 1034.983 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 76.687 | 44.8915 | 76.687 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 44.8915 | 1079.8745 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 41.234 | 1076.217 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 35.2716 | 1070.2546 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 24.4224 | 1059.4054
[5 empty] | 86 | 1033.213 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 78.457 | 45.6358 | 78.457 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 45.6358 | 1078.8488 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 41.8603 | 1075.0733 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 35.7056 | 1068.9186 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 24.5064 | 1057.7194
[5 empty] | 88 | 1031.188 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 80.482 | 46.6352 | 80.482 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 46.6352 | 1077.8232 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 42.7417 | 1073.9297 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 36.3946 | 1067.5826 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 24.8455 | 1056.0335
[5 empty] | 90 | 1029.08 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 82.59 | 47.7175 | 82.59 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 47.7175 | 1076.7975 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 43.706 | 1072.786 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 37.1666 | 1066.2466 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 25.2675 | 1054.3475
[5 empty] | 92 | 1026.322 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 85.348 | 49.4499 | 85.348 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 49.4499 | 1075.7719 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 45.3204 | 1071.6424 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 38.5886 | 1064.9106 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 26.3395 | 1052.6615
[5 empty] | 94 | 1023.207 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 88.463 | 51.5392 | 88.463 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 51.5392 | 1074.7462 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 47.2918 | 1070.4988 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 40.3677 | 1063.5747 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.7686 | 1050.9756
[5 empty] | 96 | 1021.503 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 90.167 | 52.2175 | 90.167 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 52.2175 | 1073.7205 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 47.8521 | 1069.3551 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 40.7357 | 1062.2387 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.7866 | 1049.2896
[5 empty] | 98 | 1019.765 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 91.905 | 52.9299 | 91.905 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 52.9299 | 1072.6949 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 48.4465 | 1068.2115 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 41.1377 | 1060.9027 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.8387 | 1047.6037
[5 empty] | 100 | 1018.493 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 93.177 | 53.1762 | 93.177 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 53.1762 | 1071.6692 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 48.5748 | 1067.0678 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 41.0737 | 1059.5667 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.4247 | 1045.9177
[5 empty] | 102 | 1016.444 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 95.226 | 54.1996 | 95.226 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 54.1996 | 1070.6436 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 49.4802 | 1065.9242 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 41.7867 | 1058.2307 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.7878 | 1044.2318
[5 empty] | 104 | 1013.288 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 98.382 | 56.3299 | 98.382 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 56.3299 | 1069.6179 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 51.4925 | 1064.7805 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 43.6068 | 1056.8948 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 29.2578 | 1042.5458
[5 empty] | 106 | 1007.843 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 103.827 | 60.7492 | 103.827 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 60.7492 | 1068.5922 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 55.7939 | 1063.6369 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 47.7158 | 1055.5588 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 33.0169 | 1040.8599
[5 empty] | 108 | 1001.282 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 110.388 | 66.2846 | 110.388 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 66.2846 | 1067.5666 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 61.2112 | 1062.4932 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 52.9408 | 1054.2228 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 37.8919 | 1039.1739
[5 empty] | 110 | 996.609 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.061 | 69.9319 | 115.061 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 69.9319 | 1066.5409 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 64.7406 | 1061.3496 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 56.2778 | 1052.8868 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 40.8789 | 1037.4879
[5 empty] | 112 | 992.999 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 118.671 | 72.5163 | 118.671 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 72.5163 | 1065.5153 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 67.2069 | 1060.2059 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 58.5518 | 1051.5508 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 42.803 | 1035.802
[5 empty] | 114 | 993.639 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 118.031 | 70.8506 | 118.031 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 70.8506 | 1064.4896 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 65.4233 | 1059.0623 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 56.5758 | 1050.2148 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 40.477 | 1034.116
[5 empty] | 116 | 994.611 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 117.059 | 68.8529 | 117.059 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 68.8529 | 1063.4639 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 63.3077 | 1057.9187 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 54.2679 | 1048.8789 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 37.8191 | 1032.4301
[5 empty] | 118 | 995.751 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.919 | 66.6873 | 115.919 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 66.6873 | 1062.4383 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 61.024 | 1056.775 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 51.7919 | 1047.5429 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 34.9931 | 1030.7441
[5 empty] | 120 | 996.479 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.191 | 64.9336 | 115.191 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 64.9336 | 1061.4126 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 59.1524 | 1055.6314 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 49.7279 | 1046.2069 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 32.5792 | 1029.0582
[5 empty] | 122 | 996.147 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 115.523 | 64.2399 | 115.523 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 64.2399 | 1060.3869 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 58.3407 | 1054.4877 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 48.7239 | 1044.8709 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 31.2252 | 1027.3722
[5 empty] | 124 | 992.094 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 119.576 | 67.2673 | 119.576 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 67.2673 | 1059.3613 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 61.2501 | 1053.3441 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 51.4409 | 1043.5349 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 33.5923 | 1025.6863
[5 empty] | 126 | 985.623 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 126.047 | 72.7126 | 126.047 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 72.7126 | 1058.3356 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 66.5774 | 1052.2004 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 56.576 | 1042.199 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 38.3773 | 1024.0003
[5 empty] | 128 | 977.759 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 133.911 | 79.551 | 133.911 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 79.551 | 1057.31 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 73.2978 | 1051.0568 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 63.104 | 1040.863 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 44.5553 | 1022.3143
[5 empty] | 130 | 969.772 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 141.898 | 86.5123 | 141.898 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 86.5123 | 1056.2843 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 80.1411 | 1049.9131 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 69.755 | 1039.527 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 50.8564 | 1020.6284
[5 empty] | 132 | 981.785 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 129.885 | 73.4736 | 129.885 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 73.4736 | 1055.2586 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 66.9845 | 1048.7695 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 56.406 | 1038.191 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 37.1574 | 1018.9424
[5 empty] | 134 | 991.458 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 120.212 | 62.775 | 120.212 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 62.775 | 1054.233 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 56.1678 | 1047.6258 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 45.397 | 1036.855 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 25.7985 | 1017.2565
[5 empty] | 136 | 987.77 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 123.9 | 65.4373 | 123.9 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 65.4373 | 1053.2073 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 58.7122 | 1046.4822 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 47.749 | 1035.519 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 27.8005 | 1015.5705
[5 empty] | 138 | 982.725 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 128.945 | 69.4567 | 128.945 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 69.4567 | 1052.1817 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 62.6136 | 1045.3386 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 51.4581 | 1034.1831 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 31.1596 | 1013.8846
[5 empty] | 140 | 977.559 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 134.111 | 73.597 | 134.111 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 73.597 | 1051.156 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 66.6359 | 1044.1949 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 55.2881 | 1032.8471 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 34.6396 | 1012.1986
[5 empty] | 142 | 975.289 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 136.381 | 74.8413 | 136.381 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 74.8413 | 1050.1303 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 67.7623 | 1043.0513 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 56.2221 | 1031.5111 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 35.2237 | 1010.5127
[5 empty] | 144 | 973.968 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 137.702 | 75.1367 | 137.702 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 75.1367 | 1049.1047 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 67.9396 | 1041.9076 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 56.2071 | 1030.1751 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 34.8587 | 1008.8267
[5 empty] | 146 | 962.473 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 149.197 | 85.606 | 149.197 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 85.606 | 1048.079 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 78.291 | 1040.764 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 66.3661 | 1028.8391 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 44.6677 | 1007.1407
[5 empty] | 148 | 951.285 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 160.385 | 95.7684 | 160.385 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 95.7684 | 1047.0534 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 88.3353 | 1039.6203 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 76.2182 | 1027.5032 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 54.1698 | 1005.4548
[5 empty] | 150 | 948.174 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 163.496 | 97.8537 | 163.496 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 97.8537 | 1046.0277 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 90.3027 | 1038.4767 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 77.9932 | 1026.1672 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 55.5948 | 1003.7688
[5 empty] | 152 | 944.641 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 167.029 | 100.361 | 167.029 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 100.361 | 1045.002 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 92.692 | 1037.333 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 80.1902 | 1024.8312 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 57.4419 | 1002.0829
[5 empty] | 154 | 941.566 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 170.104 | 102.4104 | 170.104 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 102.4104 | 1043.9764 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 94.6234 | 1036.1894 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 81.9292 | 1023.4952 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 58.8309 | 1000.3969
[5 empty] | 156 | 940.942 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 170.728 | 102.0087 | 170.728 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 102.0087 | 1042.9507 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 94.1037 | 1035.0457 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 81.2172 | 1022.1592 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 57.769 | 998.711
[5 empty] | 158 | 939.726 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 171.944 | 102.199 | 171.944 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 102.199 | 1041.925 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 94.1761 | 1033.9021 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 81.0972 | 1020.8232 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 57.299 | 997.025
[5 empty] | 160 | 936.738 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 174.932 | 104.1614 | 174.932 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 104.1614 | 1040.8994 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 96.0204 | 1032.7584 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 82.7493 | 1019.4873 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 58.6011 | 995.3391
[5 empty] | 162 | 933.65 | 2 | 1.9 | 4.0831 | 1.4401 | 2421411.635 | 178.02 | 106.2237 | 178.02 | 11.875 | 1105894.9783 | 0.00867 | 0.96468 | 0.060983 | 1.0257 | 0 | 106.2237 | 1039.8737 | 0.0097304 | 1.0827 | 0.060983 | 1.1436 | 0 | 97.9648 | 1031.6148 | 0.011459 | 1.275 | 0.060983 | 1.336 | 0 | 84.5013 | 1018.1513 | 0.014543 | 1.625 | 0.060983 | 1.686 | 0 | 60.0031 | 993.6531
[5 empty] | 164 | 932.745 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.925 | 105.7778 | 178.925 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 105.7778 | 1038.5228 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 97.3621 | 1030.1071 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 83.6429 | 1016.3879 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 58.6781 | 991.4231
[5 empty] | 166 | 931.696 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 179.974 | 105.4758 | 179.974 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 105.4758 | 1037.1718 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 96.9035 | 1028.5995 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 82.9285 | 1014.6245 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 57.4971 | 989.1931
[5 empty] | 168 | 930.999 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.671 | 104.8219 | 180.671 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 104.8219 | 1035.8209 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 96.0928 | 1027.0918 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 81.8621 | 1012.8611 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.964 | 986.963
[5 empty] | 170 | 930.885 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.785 | 103.5849 | 180.785 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 103.5849 | 1034.4699 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 94.6991 | 1025.5841 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 80.2127 | 1011.0977 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 53.848 | 984.733
[5 empty] | 172 | 930.378 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 181.292 | 102.741 | 181.292 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 102.741 | 1033.119 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 93.6985 | 1024.0765 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 78.9563 | 1009.3343 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 52.125 | 982.503
[5 empty] | 174 | 931.324 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.346 | 100.444 | 180.346 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 100.444 | 1031.768 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 91.2448 | 1022.5688 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 76.2469 | 1007.5709 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 48.949 | 980.273
[5 empty] | 176 | 933.53 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.14 | 96.887 | 178.14 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 96.887 | 1030.417 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 87.5311 | 1021.0611 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 72.2775 | 1005.8075 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 44.513 | 978.043
[5 empty] | 178 | 932.714 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.956 | 96.3521 | 178.956 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 96.3521 | 1029.0661 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 86.8394 | 1019.5534 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 71.3301 | 1004.0441 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 43.099 | 975.813
[5 empty] | 180 | 928.311 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.359 | 99.4041 | 183.359 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 99.4041 | 1027.7151 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 89.7348 | 1018.0458 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 73.9697 | 1002.2807 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 45.272 | 973.583
[5 empty] | 182 | 924.179 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 187.491 | 102.1852 | 187.491 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 102.1852 | 1026.3642 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 92.3591 | 1016.5381 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 76.3383 | 1000.5173 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 47.1739 | 971.3529
[5 empty] | 184 | 928.398 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.272 | 96.6152 | 183.272 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 96.6152 | 1025.0132 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 86.6324 | 1015.0304 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 70.3559 | 998.7539 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 40.7249 | 969.1229
[5 empty] | 186 | 930.866 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.804 | 92.7963 | 180.804 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 92.7963 | 1023.6623 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 82.6568 | 1013.5228 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 66.1245 | 996.9905 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 36.0269 | 966.8929
[5 empty] | 188 | 928.411 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.259 | 93.9003 | 183.259 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 93.9003 | 1022.3113 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 83.6041 | 1012.0151 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 66.8161 | 995.2271 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 36.2519 | 964.6629
[5 empty] | 190 | 927.849 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.821 | 93.1114 | 183.821 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 93.1114 | 1020.9604 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 82.6584 | 1010.5074 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 65.6147 | 993.4637 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 34.5839 | 962.4329
[5 empty] | 192 | 926.71 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 184.96 | 92.8994 | 184.96 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 92.8994 | 1019.6094 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 82.2898 | 1008.9998 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 64.9903 | 991.7003 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 33.4929 | 960.2029
[5 empty] | 194 | 926.201 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 185.469 | 92.0575 | 185.469 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 92.0575 | 1018.2585 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 81.2911 | 1007.4921 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 63.7359 | 989.9369 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 31.7718 | 957.9728
[5 empty] | 196 | 924.509 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 187.161 | 92.3985 | 187.161 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 92.3985 | 1016.9075 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 81.4754 | 1005.9844 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 63.6645 | 988.1735 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 31.2338 | 955.7428
[5 empty] | 198 | 923.417 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 188.253 | 92.1396 | 188.253 | 11.2952 | 996509.3057 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 92.1396 | 1015.5566 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 81.0598 | 1004.4768 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 62.9931 | 986.4101 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 30.0958 | 953.5128
[5 empty] | 200 | 923.011 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 188.659 | 91.1946 | 188.659 | 11.3195 | 998644.849 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 91.1946 | 1014.2056 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 79.9581 | 1002.9691 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 61.6357 | 984.6467 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 28.2718 | 951.2828
[5 empty] | 202 | 921.969 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 189.701 | 90.8856 | 189.701 | 11.3821 | 1004125.4583 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 90.8856 | 1012.8546 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 79.4924 | 1001.4614 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 60.9143 | 982.8833 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 27.0838 | 949.0528
[5 empty] | 204 | 920.661 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 191.009 | 90.8427 | 191.009 | 11.4605 | 1011004.6025 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 90.8427 | 1011.5037 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 79.2927 | 999.9537 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 60.4589 | 981.1199 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 26.1618 | 946.8228
[5 empty] | 206 | 920.243 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 191.427 | 89.9097 | 191.427 | 11.4856 | 1013202.8554 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 89.9097 | 1010.1527 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 78.2031 | 998.4461 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 59.1136 | 979.3566 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 24.3497 | 944.5927
[5 empty] | 208 | 919.297 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 192.373 | 89.5048 | 192.373 | 11.5424 | 1018177.6195 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 89.5048 | 1008.8018 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 77.6414 | 996.9384 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 58.2962 | 977.5932 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 23.0657 | 942.3627
[5 empty] | 210 | 917.533 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 194.137 | 89.9178 | 194.137 | 11.6482 | 1027453.1808 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 89.9178 | 1007.4508 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 77.8977 | 995.4307 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 58.2968 | 975.8298 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 22.5997 | 940.1327
[5 empty] | 212 | 917.684 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 193.986 | 88.4159 | 193.986 | 11.6392 | 1026659.2276 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 88.4159 | 1006.0999 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 76.2391 | 993.9231 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 56.3824 | 974.0664 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 20.2187 | 937.9027
[5 empty] | 214 | 915.724 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 195.946 | 89.0249 | 195.946 | 11.7568 | 1036964.2159 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 89.0249 | 1004.7489 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 76.6914 | 992.4154 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 56.579 | 972.303 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 19.9487 | 935.6727
[5 empty] | 216 | 915.73 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 195.94 | 87.668 | 195.94 | 11.7564 | 1036932.6721 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 87.668 | 1003.398 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 75.1777 | 990.9077 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 54.8096 | 970.5396 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 17.7127 | 933.4427
[5 empty] | 218 | 915.584 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 196.086 | 86.463 | 196.086 | 11.7652 | 1037700.2343 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 86.463 | 1002.047 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 73.8161 | 989.4001 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 53.1922 | 968.7762 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 15.6286 | 931.2126
[5 empty] | 220 | 915.444 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 196.226 | 85.2521 | 196.226 | 11.7736 | 1038436.2457 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 85.2521 | 1000.6961 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 72.4484 | 987.8924 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 51.5688 | 967.0128 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 13.5386 | 928.9826
[5 empty] | 222 | 913.52 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 198.15 | 85.8251 | 198.15 | 11.889 | 1048550.4405 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 85.8251 | 999.3451 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 72.8647 | 986.3847 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 51.7294 | 965.2494 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 13.2326 | 926.7526
[5 empty] | 224 | 912.524 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 199.146 | 85.4702 | 199.146 | 11.9488 | 1053785.7546 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 85.4702 | 997.9942 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 72.3531 | 984.8771 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 50.962 | 963.486 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 11.9986 | 924.5226
[5 empty] | 226 | 912.565 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | 199.105 | 84.6392 | 199.105 | 13.2737 | 1300704.0144 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 84.6392 | 997.2042 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 71.432 | 983.997 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 49.8941 | 962.4591 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 10.6643 | 923.2293
|  |  |  | Reservoir | 228 | 913.484 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 10 | 130 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 120 | 10 | 1043.484 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 120 | 130 | 1043.484 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 120 | 130 | 1043.484 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 120 | 130 | 1043.484
[5 empty] | 230 | 913.545 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 129.149 | 129.0589 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 129.149 | 1042.694 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 129.0589 | 1042.6039 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 128.9121 | 1042.4571 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 128.6457 | 1042.1907
[5 empty] | 232 | 914.546 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 127.3581 | 127.1778 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 127.3581 | 1041.9041 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 127.1778 | 1041.7238 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 126.8842 | 1041.4302 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 126.3514 | 1040.8974
[5 empty] | 234 | 918.285 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 122.8291 | 122.5587 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 122.8291 | 1041.1141 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 122.5587 | 1040.8437 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 122.1183 | 1040.4033 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 121.319 | 1039.604
[5 empty] | 236 | 919.357 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 120.9671 | 120.6066 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 120.9671 | 1040.3241 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 120.6066 | 1039.9636 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 120.0194 | 1039.3764 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 118.9537 | 1038.3107
[5 empty] | 238 | 918.649 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 120.8852 | 120.4345 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 120.8852 | 1039.5342 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 120.4345 | 1039.0835 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 119.7005 | 1038.3495 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 118.3684 | 1037.0174
[5 empty] | 240 | 922.974 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 115.7702 | 115.2294 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 115.7702 | 1038.7442 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 115.2294 | 1038.2034 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 114.3486 | 1037.3226 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 112.7501 | 1035.7241
[5 empty] | 242 | 927.375 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 110.5792 | 109.9483 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 110.5792 | 1037.9542 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 109.9483 | 1037.3233 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 108.9207 | 1036.2957 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 107.0557 | 1034.4307
[5 empty] | 244 | 929.253 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 107.9113 | 107.1902 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 107.9113 | 1037.1643 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 107.1902 | 1036.4432 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 106.0158 | 1035.2688 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 103.8844 | 1033.1374
[5 empty] | 246 | 930.863 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 105.5113 | 104.7001 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 105.5113 | 1036.3743 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 104.7001 | 1035.5631 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 103.3789 | 1034.2419 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 100.9811 | 1031.8441
[5 empty] | 248 | 931.924 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 103.6603 | 102.759 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 103.6603 | 1035.5843 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 102.759 | 1034.683 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 101.291 | 1033.215 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 98.6268 | 1030.5508
[5 empty] | 250 | 936.722 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 98.0724 | 97.0809 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 98.0724 | 1034.7944 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 97.0809 | 1033.8029 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 95.4661 | 1032.1881 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 92.5354 | 1029.2574
[5 empty] | 252 | 941.777 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 92.2274 | 91.1458 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 92.2274 | 1034.0044 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 91.1458 | 1032.9228 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 89.3842 | 1031.1612 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 86.1871 | 1027.9641
[5 empty] | 254 | 948.143 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 85.0714 | 83.8997 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 85.0714 | 1033.2144 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 83.8997 | 1032.0427 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 81.9913 | 1030.1343 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 78.5278 | 1026.6708
[5 empty] | 256 | 955.417 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 77.0075 | 75.7456 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 77.0075 | 1032.4245 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 75.7456 | 1031.1626 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 73.6904 | 1029.1074 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 69.9605 | 1025.3775
[5 empty] | 258 | 962.7 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 68.9345 | 67.5825 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 68.9345 | 1031.6345 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 67.5825 | 1030.2825 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 65.3805 | 1028.0805 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 61.3842 | 1024.0842
[5 empty] | 260 | 969.281 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 61.5635 | 60.1214 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 61.5635 | 1030.8445 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 60.1214 | 1029.4024 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 57.7726 | 1027.0536 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 53.5098 | 1022.7908
[5 empty] | 262 | 980.284 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 49.7706 | 48.2383 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 49.7706 | 1030.0546 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 48.2383 | 1028.5223 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 45.7427 | 1026.0267 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 41.2135 | 1021.4975
[5 empty] | 264 | 986.551 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 42.7136 | 41.0912 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 42.7136 | 1029.2646 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 41.0912 | 1027.6422 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 38.4488 | 1024.9998 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 33.6532 | 1020.2042
[5 empty] | 266 | 989.198 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 39.2767 | 37.5641 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 39.2767 | 1028.4747 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 37.5641 | 1026.7621 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 34.775 | 1023.973 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 29.7129 | 1018.9109
[5 empty] | 268 | 994.39 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 33.2947 | 31.492 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 33.2947 | 1027.6847 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 31.492 | 1025.882 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 28.5561 | 1022.9461 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 23.2275 | 1017.6175
[5 empty] | 270 | 999.917 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 26.9777 | 25.0849 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 26.9777 | 1026.8947 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 25.0849 | 1025.0019 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 22.0022 | 1021.9192 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 16.4072 | 1016.3242
[5 empty] | 272 | 1004.623 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 21.4818 | 19.4988 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 21.4818 | 1026.1048 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 19.4988 | 1024.1218 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 16.2693 | 1020.8923 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 10.4079 | 1015.0309
|  |  |  | Reservoir | 274 | 1008.819 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 10 | 170 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 160 | 10 | 1178.819 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 160 | 170 | 1178.819 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 160 | 170 | 1178.819 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 160 | 170 | 1178.819
[5 empty] | 276 | 1007.834 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 170.195 | 170.1049 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 170.195 | 1178.029 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 170.1049 | 1177.9389 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 169.9581 | 1177.7921 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 169.6917 | 1177.5257
[5 empty] | 278 | 1005.626 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 171.6131 | 171.4328 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 171.6131 | 1177.2391 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 171.4328 | 1177.0588 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 171.1392 | 1176.7652 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 170.6064 | 1176.2324
[5 empty] | 280 | 1001.623 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 174.8261 | 174.5557 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 174.8261 | 1176.4491 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 174.5557 | 1176.1787 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 174.1153 | 1175.7383 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 173.316 | 1174.939
[5 empty] | 282 | 1004.052 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 171.6071 | 171.2466 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 171.6071 | 1175.6591 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 171.2466 | 1175.2986 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 170.6594 | 1174.7114 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 169.5937 | 1173.6457
[5 empty] | 284 | 1010.797 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 164.0722 | 163.6215 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 164.0722 | 1174.8692 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 163.6215 | 1174.4185 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 162.8875 | 1173.6845 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 161.5554 | 1172.3524
[5 empty] | 286 | 1014.67 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 159.4092 | 158.8684 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 159.4092 | 1174.0792 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 158.8684 | 1173.5384 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 157.9876 | 1172.6576 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 156.3891 | 1171.0591
[5 empty] | 288 | 1017.319 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 155.9702 | 155.3393 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 155.9702 | 1173.2892 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 155.3393 | 1172.6583 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 154.3117 | 1171.6307 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 152.4467 | 1169.7657
[5 empty] | 290 | 1027.459 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 145.0403 | 144.3192 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 145.0403 | 1172.4993 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 144.3192 | 1171.7782 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 143.1448 | 1170.6038 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 141.0134 | 1168.4724
[5 empty] | 292 | 1031.99 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 139.7193 | 138.9081 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 139.7193 | 1171.7093 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 138.9081 | 1170.8981 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 137.5869 | 1169.5769 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 135.1891 | 1167.1791
[5 empty] | 294 | 1036.254 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 134.6653 | 133.764 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 134.6653 | 1170.9193 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 133.764 | 1170.018 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 132.296 | 1168.55 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 129.6318 | 1165.8858
[5 empty] | 296 | 1040.127 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 130.0024 | 129.0109 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 130.0024 | 1170.1294 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 129.0109 | 1169.1379 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 127.3961 | 1167.5231 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 124.4654 | 1164.5924
[5 empty] | 298 | 1044.396 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 124.9434 | 123.8618 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 124.9434 | 1169.3394 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 123.8618 | 1168.2578 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 122.1002 | 1166.4962 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 118.9031 | 1163.2991
[5 empty] | 300 | 1051.339 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 117.2104 | 116.0387 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 117.2104 | 1168.5494 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 116.0387 | 1167.3777 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 114.1303 | 1165.4693 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 110.6668 | 1162.0058
[5 empty] | 302 | 1060.955 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 106.8045 | 105.5426 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 106.8045 | 1167.7595 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 105.5426 | 1166.4976 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 103.4874 | 1164.4424 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 99.7575 | 1160.7125
[5 empty] | 304 | 1070.227 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 96.7425 | 95.3905 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 96.7425 | 1166.9695 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 95.3905 | 1165.6175 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 93.1885 | 1163.4155 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 89.1922 | 1159.4192
[5 empty] | 306 | 1072.691 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 93.4885 | 92.0464 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 93.4885 | 1166.1795 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 92.0464 | 1164.7374 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 89.6976 | 1162.3886 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 85.4348 | 1158.1258
[5 empty] | 308 | 1076.503 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 88.8866 | 87.3543 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 88.8866 | 1165.3896 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 87.3543 | 1163.8573 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 84.8587 | 1161.3617 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 80.3295 | 1156.8325
[5 empty] | 310 | 1083.996 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 80.6036 | 78.9812 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 80.6036 | 1164.5996 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 78.9812 | 1162.9772 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 76.3388 | 1160.3348 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 71.5432 | 1155.5392
[5 empty] | 312 | 1097.188 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 66.6217 | 64.9091 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 66.6217 | 1163.8097 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 64.9091 | 1162.0971 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 62.12 | 1159.308 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 57.0579 | 1154.2459
[5 empty] | 314 | 1103.545 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 59.4747 | 57.672 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 59.4747 | 1163.0197 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 57.672 | 1161.217 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 54.7361 | 1158.2811 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 49.4075 | 1152.9525
[5 empty] | 316 | 1105.174 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 57.0557 | 55.1629 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 57.0557 | 1162.2297 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 55.1629 | 1160.3369 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 52.0802 | 1157.2542 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 46.4852 | 1151.6592
[5 empty] | 318 | 1111.657 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 49.7828 | 47.7998 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 49.7828 | 1161.4398 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 47.7998 | 1159.4568 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 44.5703 | 1156.2273 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 38.7089 | 1150.3659
[5 empty] | 320 | 1122.935 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 37.7148 | 35.6417 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 37.7148 | 1160.6498 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 35.6417 | 1158.5767 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 32.2654 | 1155.2004 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 26.1376 | 1149.0726
[5 empty] | 322 | 1128.197 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 31.6628 | 29.4996 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 31.6628 | 1159.8598 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 29.4996 | 1157.6966 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 25.9765 | 1154.1735 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 19.5822 | 1147.7792
[5 empty] | 324 | 1132.561 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 26.5089 | 24.2555 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 26.5089 | 1159.0699 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 24.2555 | 1156.8165 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 20.5856 | 1153.1466 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 13.9249 | 1146.4859
[5 empty] | 326 | 1131.854 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 26.4259 | 24.0824 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 26.4259 | 1158.2799 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 24.0824 | 1155.9364 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 20.2657 | 1152.1197 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 13.3386 | 1145.1926
[5 empty] | 328 | 1133.338 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 24.1519 | 21.7183 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 24.1519 | 1157.4899 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 21.7183 | 1155.0563 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 17.7548 | 1151.0928 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 10.5613 | 1143.8993
|  |  |  | Reservoir | 330 | 1136.405 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 10 | 10 | 10 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 10 | 1146.405 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 10 | 1146.405 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 10 | 1146.405 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 10 | 1146.405
[5 empty] | 332 | 1128.709 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 17.696 | 16.345 | 17.696 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 16.345 | 1145.054 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 16.1883 | 1144.8973 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 15.9326 | 1144.6416 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 15.466 | 1144.175
[5 empty] | 334 | 1120.713 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 25.692 | 22.9901 | 25.692 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 22.9901 | 1143.7031 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 22.6767 | 1143.3897 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 22.1652 | 1142.8782 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 21.232 | 1141.945
[5 empty] | 336 | 1115.226 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 31.179 | 27.1261 | 31.179 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 27.1261 | 1142.3521 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 26.656 | 1141.882 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 25.8888 | 1141.1148 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 24.489 | 1139.715
[5 empty] | 338 | 1108.709 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 37.696 | 32.2922 | 37.696 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 32.2922 | 1141.0012 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 31.6653 | 1140.3743 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 30.6424 | 1139.3514 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 28.7759 | 1137.4849
[5 empty] | 340 | 1102.499 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 43.906 | 37.1512 | 43.906 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 37.1512 | 1139.6502 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 36.3677 | 1138.8667 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 35.089 | 1137.588 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 32.7559 | 1135.2549
[5 empty] | 342 | 1096.349 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 50.056 | 41.9503 | 50.056 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 41.9503 | 1138.2993 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 41.01 | 1137.359 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 39.4756 | 1135.8246 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 36.6759 | 1133.0249
[5 empty] | 344 | 1090.39 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 56.015 | 46.5583 | 56.015 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 46.5583 | 1136.9483 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 45.4613 | 1135.8513 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 43.6712 | 1134.0612 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 40.4049 | 1130.7949
[5 empty] | 346 | 1087.765 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 58.64 | 47.8324 | 58.64 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 47.8324 | 1135.5974 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 46.5786 | 1134.3436 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 44.5328 | 1132.2978 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 40.7999 | 1128.5649
[5 empty] | 348 | 1084.661 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 61.744 | 49.5854 | 61.744 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 49.5854 | 1134.2464 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 48.175 | 1132.836 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 45.8734 | 1130.5344 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 41.6739 | 1126.3349
[5 empty] | 350 | 1081.662 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 64.743 | 51.2335 | 64.743 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 51.2335 | 1132.8955 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 49.6663 | 1131.3283 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 47.109 | 1128.771 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 42.4428 | 1124.1048
[5 empty] | 352 | 1076.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 69.533 | 54.6725 | 69.533 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 54.6725 | 1131.5445 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 52.9486 | 1129.8206 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 50.1356 | 1127.0076 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 45.0028 | 1121.8748
[5 empty] | 354 | 1070.898 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 75.507 | 59.2956 | 75.507 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 59.2956 | 1130.1936 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 57.415 | 1128.313 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 54.3462 | 1125.2442 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 48.7468 | 1119.6448
[5 empty] | 356 | 1065.018 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 81.387 | 63.8246 | 81.387 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 63.8246 | 1128.8426 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 61.7873 | 1126.8053 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 58.4628 | 1123.4808 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 52.3968 | 1117.4148
[5 empty] | 358 | 1059.58 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 86.825 | 67.9116 | 86.825 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 67.9116 | 1127.4916 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 65.7176 | 1125.2976 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 62.1374 | 1121.7174 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.6048 | 1115.1848
[5 empty] | 360 | 1055.284 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 91.121 | 70.8567 | 91.121 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 70.8567 | 1126.1407 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 68.506 | 1123.79 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 64.67 | 1119.954 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 57.6708 | 1112.9548
[5 empty] | 362 | 1050.886 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 95.519 | 73.9037 | 95.519 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 73.9037 | 1124.7897 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 71.3963 | 1122.2823 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 67.3047 | 1118.1907 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 59.8387 | 1110.7247
[5 empty] | 364 | 1052.647 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 93.758 | 70.7918 | 93.758 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 70.7918 | 1123.4388 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 68.1276 | 1120.7746 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 63.7803 | 1116.4273 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.8477 | 1108.4947
[5 empty] | 366 | 1051.117 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 95.288 | 70.9708 | 95.288 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 70.9708 | 1122.0878 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 68.15 | 1119.267 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 63.5469 | 1114.6639 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.1477 | 1106.2647
[5 empty] | 368 | 1048.266 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 98.139 | 72.4709 | 98.139 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 72.4709 | 1120.7369 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 69.4933 | 1117.7593 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 64.6345 | 1112.9005 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.7687 | 1104.0347
[5 empty] | 370 | 1040.172 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 106.233 | 79.2139 | 106.233 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 79.2139 | 1119.3859 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 76.0796 | 1116.2516 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 70.9651 | 1111.1371 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 61.6327 | 1101.8047
[5 empty] | 372 | 1033.483 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 112.922 | 84.552 | 112.922 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 84.552 | 1118.035 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 81.2609 | 1114.7439 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 75.8907 | 1109.3737 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 66.0917 | 1099.5747
[5 empty] | 374 | 1030.95 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 115.455 | 85.734 | 115.455 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 85.734 | 1116.684 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 82.2863 | 1113.2363 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 76.6603 | 1107.6103 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 66.3946 | 1097.3446
[5 empty] | 376 | 1032.263 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 114.142 | 83.0701 | 114.142 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 83.0701 | 1115.3331 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 79.4656 | 1111.7286 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 73.5839 | 1105.8469 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 62.8516 | 1095.1146
[5 empty] | 378 | 1031.391 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 115.014 | 82.5911 | 115.014 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 82.5911 | 1113.9821 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 78.8299 | 1110.2209 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 72.6925 | 1104.0835 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 61.4936 | 1092.8846
[5 empty] | 380 | 1025.791 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 120.614 | 86.8402 | 120.614 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 86.8402 | 1112.6312 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 82.9223 | 1108.7133 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 76.5291 | 1102.3201 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 64.8636 | 1090.6546
[5 empty] | 382 | 1020.911 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 125.494 | 90.3692 | 125.494 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 90.3692 | 1111.2802 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 86.2946 | 1107.2056 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 79.6457 | 1100.5567 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 67.5136 | 1088.4246
[5 empty] | 384 | 1015.65 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 130.755 | 94.2792 | 130.755 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 94.2792 | 1109.9292 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 90.0479 | 1105.6979 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 83.1433 | 1098.7933 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 70.5446 | 1086.1946
[5 empty] | 386 | 1012.139 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 134.266 | 96.4393 | 134.266 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 96.4393 | 1108.5783 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 92.0513 | 1104.1903 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 84.8909 | 1097.0299 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 71.8255 | 1083.9645
[5 empty] | 388 | 1010.472 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 135.933 | 96.7553 | 135.933 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 96.7553 | 1107.2273 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 92.2106 | 1102.6826 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 84.7945 | 1095.2665 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 71.2625 | 1081.7345
[5 empty] | 390 | 1005.401 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 141.004 | 100.4754 | 141.004 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 100.4754 | 1105.8764 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 95.7739 | 1101.1749 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 88.1021 | 1093.5031 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 74.1035 | 1079.5045
[5 empty] | 392 | 996.666 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 149.739 | 107.8594 | 149.739 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 107.8594 | 1104.5254 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 103.0013 | 1099.6673 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 95.0737 | 1091.7397 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 80.6085 | 1077.2745
[5 empty] | 394 | 991.35 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 155.055 | 111.8245 | 155.055 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 111.8245 | 1103.1745 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 106.8096 | 1098.1596 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 98.6263 | 1089.9763 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 83.6945 | 1075.0445
[5 empty] | 396 | 990.486 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 155.919 | 111.3375 | 155.919 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 111.3375 | 1101.8235 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 106.1659 | 1096.6519 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 97.7269 | 1088.2129 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 82.3285 | 1072.8145
[5 empty] | 398 | 992.761 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 153.644 | 107.7116 | 153.644 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 107.7116 | 1100.4726 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 102.3832 | 1095.1442 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 93.6885 | 1086.4495 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 77.8234 | 1070.5844
[5 empty] | 400 | 999.077 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 147.328 | 100.0446 | 147.328 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 100.0446 | 1099.1216 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 94.5596 | 1093.6366 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 85.6091 | 1084.6861 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 69.2774 | 1068.3544
[5 empty] | 402 | 1001.8 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 144.605 | 95.9707 | 144.605 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 95.9707 | 1097.7707 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 90.3289 | 1092.1289 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 81.1227 | 1082.9227 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 64.3244 | 1066.1244
[5 empty] | 404 | 1002.224 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 144.181 | 94.1957 | 144.181 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 94.1957 | 1096.4197 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 88.3972 | 1090.6212 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 78.9353 | 1081.1593 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 61.6704 | 1063.8944
[5 empty] | 406 | 1002.003 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 144.402 | 93.0658 | 144.402 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 93.0658 | 1095.0688 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 87.1106 | 1089.1136 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 77.3929 | 1079.3959 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 59.6614 | 1061.6644
[5 empty] | 408 | 1003.596 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 142.809 | 90.1218 | 142.809 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 90.1218 | 1093.7178 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 84.0099 | 1087.6059 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 74.0365 | 1077.6325 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.8384 | 1059.4344
[5 empty] | 410 | 994.111 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 152.294 | 98.2559 | 152.294 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 98.2559 | 1092.3669 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 91.9872 | 1086.0982 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 81.7581 | 1075.8691 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 63.0933 | 1057.2043
[5 empty] | 412 | 983.925 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 162.48 | 107.0909 | 162.48 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 107.0909 | 1091.0159 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 100.6656 | 1084.5906 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 90.1807 | 1074.1057 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 71.0493 | 1054.9743
[5 empty] | 414 | 972.347 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 174.058 | 117.3179 | 174.058 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 117.3179 | 1089.6649 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 110.7359 | 1083.0829 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 99.9953 | 1072.3423 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 80.3973 | 1052.7443
[5 empty] | 416 | 963.901 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 182.504 | 124.413 | 182.504 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 124.413 | 1088.314 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 117.6742 | 1081.5752 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 106.6779 | 1070.5789 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 86.6133 | 1050.5143
[5 empty] | 418 | 963.258 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 183.147 | 123.705 | 183.147 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 123.705 | 1086.963 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 116.8096 | 1080.0676 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 105.5575 | 1068.8155 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 85.0263 | 1048.2843
[5 empty] | 420 | 965.836 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.569 | 119.7761 | 180.569 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 119.7761 | 1085.6121 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 112.7239 | 1078.5599 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 101.2161 | 1067.0521 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 80.2183 | 1046.0543
[5 empty] | 422 | 966.309 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 180.096 | 117.9521 | 180.096 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 117.9521 | 1084.2611 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 110.7432 | 1077.0522 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 98.9797 | 1065.2887 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 77.5152 | 1043.8242
[5 empty] | 424 | 972.884 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 173.521 | 110.0262 | 173.521 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 110.0262 | 1082.9102 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 102.6605 | 1075.5445 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 90.6413 | 1063.5253 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 68.7102 | 1041.5942
[5 empty] | 426 | 983.972 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 162.433 | 97.5872 | 162.433 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 97.5872 | 1081.5592 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 90.0649 | 1074.0369 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 77.79 | 1061.762 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.3922 | 1039.3642
[5 empty] | 428 | 994.096 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 152.309 | 86.1123 | 152.309 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 86.1123 | 1080.2083 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 78.4332 | 1072.5292 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 65.9026 | 1059.9986 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 43.0382 | 1037.1342
[5 empty] | 430 | 991.695 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 154.71 | 87.1623 | 154.71 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 87.1623 | 1078.8573 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 79.3265 | 1071.0215 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 66.5402 | 1058.2352 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 43.2092 | 1034.9042
[5 empty] | 432 | 984.933 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 161.472 | 92.5734 | 161.472 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 92.5734 | 1077.5064 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 84.5809 | 1069.5139 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 71.5388 | 1056.4718 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 47.7412 | 1032.6742
[5 empty] | 434 | 978.185 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 168.22 | 97.9704 | 168.22 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 97.9704 | 1076.1554 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 89.8212 | 1068.0062 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 76.5234 | 1054.7084 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 52.2591 | 1030.4441
[5 empty] | 436 | 972.686 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 173.719 | 102.1185 | 173.719 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 102.1185 | 1074.8045 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 93.8125 | 1066.4985 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 80.259 | 1052.945 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.5281 | 1028.2141
[5 empty] | 438 | 966.824 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 179.581 | 106.6295 | 179.581 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 106.6295 | 1073.4535 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 98.1669 | 1064.9909 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 84.3576 | 1051.1816 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 59.1601 | 1025.9841
[5 empty] | 440 | 960.902 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 185.503 | 111.2005 | 185.503 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 111.2005 | 1072.1025 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 102.5812 | 1063.4832 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 88.5162 | 1049.4182 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 62.8521 | 1023.7541
[5 empty] | 442 | 952.924 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 193.481 | 117.8276 | 193.481 | 11.6089 | 1024003.8948 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 117.8276 | 1070.7516 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 109.0515 | 1061.9755 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 94.7308 | 1047.6548 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 68.6001 | 1021.5241
[5 empty] | 444 | 945.683 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 200.722 | 123.7176 | 200.722 | 12.0433 | 1062069.0259 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 123.7176 | 1069.4006 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 114.7849 | 1060.4679 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 100.2084 | 1045.8914 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 73.6111 | 1019.2941
[5 empty] | 446 | 941.042 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 205.363 | 127.0077 | 205.363 | 12.3218 | 1086456.4548 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 127.0077 | 1068.0497 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 117.9182 | 1058.9602 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 103.086 | 1044.128 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 76.022 | 1017.064
[5 empty] | 448 | 937.104 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 209.301 | 129.5947 | 209.301 | 12.5581 | 1107143.7754 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 129.5947 | 1066.6987 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 120.3485 | 1057.4525 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 105.2606 | 1042.3646 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 77.73 | 1014.834
[5 empty] | 450 | 939.943 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 206.462 | 125.4048 | 206.462 | 12.3877 | 1092230.3367 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 125.4048 | 1065.3478 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 116.0018 | 1055.9448 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 100.6582 | 1040.6012 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 72.661 | 1012.604
[5 empty] | 452 | 944.776 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 201.629 | 119.2208 | 201.629 | 12.0977 | 1066835.7118 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 119.2208 | 1063.9968 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 109.6612 | 1054.4372 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 94.0618 | 1038.8378 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 65.598 | 1010.374
[5 empty] | 454 | 947.762 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 198.643 | 114.8839 | 198.643 | 11.9186 | 1051141.8599 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 114.8839 | 1062.6459 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 105.1675 | 1052.9295 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 89.3124 | 1037.0744 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 60.382 | 1008.144
[5 empty] | 456 | 952.649 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 193.756 | 108.6459 | 193.756 | 11.6254 | 1025449.8793 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 108.6459 | 1061.2949 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 98.7728 | 1051.4218 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 82.662 | 1035.311 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 53.265 | 1005.914
[5 empty] | 458 | 954.554 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 191.851 | 105.39 | 191.851 | 11.5111 | 1015432.5987 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 105.39 | 1059.944 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 95.3602 | 1049.9142 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 78.9936 | 1033.5476 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 49.1299 | 1003.6839
[5 empty] | 460 | 952.37 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 194.035 | 106.223 | 194.035 | 11.6421 | 1026916.8689 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 106.223 | 1058.593 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 96.0365 | 1048.4065 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 79.4142 | 1031.7842 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 49.0839 | 1001.4539
[5 empty] | 462 | 947.552 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 198.853 | 109.6901 | 198.853 | 11.9312 | 1052245.6837 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 109.6901 | 1057.2421 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 99.3468 | 1046.8988 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 82.4688 | 1030.0208 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 51.6719 | 999.2239
[5 empty] | 464 | 941.898 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 204.507 | 113.9931 | 204.507 | 12.2704 | 1081958.9394 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 113.9931 | 1055.8911 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 103.4932 | 1045.3912 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 86.3594 | 1028.2574 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.0959 | 996.9939
[5 empty] | 466 | 940.521 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 205.884 | 114.0191 | 205.884 | 12.353 | 1089193.7171 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 114.0191 | 1054.5401 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 103.3625 | 1043.8835 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 85.973 | 1026.494 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 54.2429 | 994.7639
[5 empty] | 468 | 939.702 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 206.703 | 113.4872 | 206.703 | 12.4022 | 1093496.4355 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 113.4872 | 1053.1892 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 102.6738 | 1042.3758 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 85.0286 | 1024.7306 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 52.8319 | 992.5339
[5 empty] | 470 | 937.147 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 209.258 | 114.6912 | 209.258 | 12.5555 | 1106917.9151 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 114.6912 | 1051.8382 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 103.7212 | 1040.8682 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 85.8202 | 1022.9672 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 53.1568 | 990.3038
[5 empty] | 472 | 933.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 212.533 | 116.6153 | 212.533 | 12.752 | 1124118.1827 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 116.6153 | 1050.4873 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 105.4885 | 1039.3605 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 87.3318 | 1021.2038 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 54.2018 | 988.0738
[5 empty] | 474 | 933.184 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 213.221 | 115.9523 | 213.221 | 12.7933 | 1127731.0678 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 115.9523 | 1049.1363 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 104.6688 | 1037.8528 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 86.2564 | 1019.4404 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 52.6598 | 985.8438
[5 empty] | 476 | 939.292 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 207.113 | 108.4934 | 207.113 | 12.4268 | 1095650.332 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 108.4934 | 1047.7854 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 97.0531 | 1036.3451 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 78.385 | 1017.677 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 44.3218 | 983.6138
[5 empty] | 478 | 944.619 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 201.786 | 101.8154 | 201.786 | 12.1072 | 1067660.7865 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 101.8154 | 1046.4344 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 90.2185 | 1034.8375 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 71.2946 | 1015.9136 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 36.7648 | 981.3838
[5 empty] | 480 | 954.023 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 192.382 | 91.0605 | 192.382 | 11.5429 | 1018224.9466 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 91.0605 | 1045.0835 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 79.3068 | 1033.3298 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 60.1272 | 1014.1502 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 25.1308 | 979.1538
[5 empty] | 482 | 968.263 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 178.142 | 75.4695 | 178.142 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 75.4695 | 1043.7325 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 63.5591 | 1031.8221 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 44.1238 | 1012.3868 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 8.6607 | 976.9237
[5 empty] | 484 | 970.384 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 176.021 | 71.9976 | 176.021 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 71.9976 | 1042.3816 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 59.9305 | 1030.3145 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 40.2394 | 1010.6234 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 4.3097 | 974.6937
[5 empty] | 486 | 964.636 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 181.769 | 76.3946 | 181.769 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 76.3946 | 1041.0306 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 64.1708 | 1028.8068 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 44.224 | 1008.86 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 7.8277 | 972.4637
[5 empty] | 488 | 956.631 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 189.774 | 83.0487 | 189.774 | 11.3864 | 1004509.4021 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 83.0487 | 1039.6797 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 70.6681 | 1027.2991 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 50.4657 | 1007.0967 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 13.6027 | 970.2337
[5 empty] | 490 | 947.426 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 198.979 | 90.9027 | 198.979 | 11.9387 | 1052907.9705 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 90.9027 | 1038.3287 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 78.3655 | 1025.7915 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 57.9073 | 1005.3333 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 20.5777 | 968.0037
[5 empty] | 492 | 941.72 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 204.685 | 95.2577 | 204.685 | 12.2811 | 1082894.1918 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 95.2577 | 1036.9777 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 82.5638 | 1024.2838 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 61.8499 | 1003.5699 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 24.0537 | 965.7737
[5 empty] | 494 | 935.985 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 210.42 | 99.6418 | 210.42 | 12.6252 | 1113021.1636 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 99.6418 | 1035.6268 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 86.7911 | 1022.7761 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 65.8215 | 1001.8065 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 27.5586 | 963.5436
[5 empty] | 496 | 930.475 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 215.93 | 103.8008 | 215.93 | 12.9558 | 1141955.1687 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 103.8008 | 1034.2758 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 90.7935 | 1021.2685 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 69.5681 | 1000.0431 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 30.8386 | 961.3136
[5 empty] | 498 | 927.611 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 218.794 | 105.3139 | 218.794 | 13.1276 | 1156990.2914 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 105.3139 | 1032.9249 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 92.1498 | 1019.7608 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 70.6687 | 998.2797 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 31.4726 | 959.0836
[5 empty] | 500 | 931.256 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 215.149 | 100.3179 | 215.149 | 12.9089 | 1137854.6524 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 100.3179 | 1031.5739 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 86.9971 | 1018.2531 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 65.2603 | 996.5163 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 25.5976 | 956.8536
[5 empty] | 502 | 920.044 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 226.361 | 110.179 | 226.361 | 13.5817 | 1196700.7082 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 110.179 | 1030.223 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 96.7014 | 1016.7454 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 74.7089 | 994.7529 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 34.5796 | 954.6236
[5 empty] | 504 | 911.78 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 234.625 | 117.092 | 234.625 | 14.0775 | 1240045.6405 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 117.092 | 1028.872 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 103.4578 | 1015.2378 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 81.2095 | 992.9895 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 40.6136 | 952.3936
[5 empty] | 506 | 907.989 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | 238.416 | 119.5321 | 238.416 | 14.305 | 1259921.4366 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 119.5321 | 1027.5211 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 105.7411 | 1013.7301 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 83.2371 | 991.2261 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 42.1746 | 950.1636
[5 empty] | 508 | 907.289 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 239.116 | 116.8057 | 239.116 | 11.9558 | 877493.6815 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 116.8057 | 1024.0947 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 102.6064 | 1009.8954 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 79.4337 | 986.7227 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 37.1389 | 944.4279
[5 empty] | 510 | 900.577 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 245.828 | 120.0914 | 245.828 | 12.2914 | 901921.523 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 120.0914 | 1020.6684 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 105.4837 | 1006.0607 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 81.6424 | 982.2194 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 38.1152 | 938.6922
[5 empty] | 512 | 902.112 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 244.293 | 115.1301 | 244.293 | 12.2147 | 896335.9807 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 115.1301 | 1017.2421 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 100.114 | 1002.226 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 75.6041 | 977.7161 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 30.8446 | 932.9566
[5 empty] | 514 | 900.179 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 246.226 | 113.6367 | 246.226 | 12.3113 | 903369.6664 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 113.6367 | 1013.8157 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 98.2123 | 998.3913 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 73.0337 | 973.2127 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 27.0419 | 927.2209
[5 empty] | 516 | 903.811 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 242.594 | 106.5784 | 242.594 | 12.1297 | 890152.9994 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 106.5784 | 1010.3894 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 90.7456 | 994.5566 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 64.8984 | 968.7094 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 17.6743 | 921.4853
[5 empty] | 518 | 910.027 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 236.378 | 96.9361 | 236.378 | 11.8189 | 867525.7369 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 96.9361 | 1006.9631 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 80.6949 | 990.7219 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 54.179 | 964.206 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 5.7226 | 915.7496
|  |  |  | Reservoir | 520 | 911.131 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 10 | 235.274 | 10 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 235.274 | 921.131 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 10 | 921.131 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 10 | 921.131 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 10 | 921.131
[15 empty] | Total Steel Mass (kg): | 280875664.0658