## Summary
Option1 Summary
Item | Chainage | Value
Pipeline | 0-8 | 2.2 | m - Diameter
Pump Station | 8 | 200 | m - Pumping head
Pipeline | 8-322 | 2.2 | m - Diameter
Pipeline | 322-356 | 2 | m - Diameter
Pipeline | 356-504 | 1.8 | m - Diameter
Pipeline | 504-520 | 1.5 | m - Diameter

## Control Points
Longitudinal profile data - Botswana pipeline
| OPTION 1: Pipeline goes through Serule before joining to BPT1 | OPTION2: Pipeline goes directly to BPT1
CHAINAGE (km0 | NGL (m) | NGL (m) |  | Botswana 1
2 | 1069.018 | 1069.018 | Start | Botswana 2
4 | 1067.321 | 1067.321
6 | 1064.035 | 1064.035
8 | 1063.832 | 1063.832
10 | 1067.893 | 1067.893
12 | 1075.133 | 1075.133
14 | 1082.768 | 1082.768
16 | 1089.726 | 1089.726
18 | 1094.131 | 1094.131
20 | 1097.897 | 1097.897
22 | 1101.67 | 1101.67
24 | 1095.952 | 1095.952
26 | 1090.107 | 1090.107
28 | 1085.781 | 1085.781
30 | 1081.89 | 1081.89
32 | 1077.937 | 1077.937
34 | 1074.89 | 1074.89
36 | 1071.114 | 1071.114
38 | 1065.311 | 1065.311
40 | 1059.051 | 1059.051
42 | 1054.28 | 1054.28
44 | 1053.871 | 1053.871
46 | 1050.42 | 1050.42
48 | 1052.704 | 1052.704
50 | 1056.355 | 1056.355
52 | 1058.466 | 1058.466
54 | 1055.99 | 1055.99
56 | 1055.66 | 1055.66
58 | 1056.404 | 1056.404
60 | 1056.841 | 1056.841
62 | 1056.377 | 1056.377
64 | 1052.503 | 1052.503
66 | 1046.022 | 1046.022
68 | 1036.575 | 1036.575
70 | 1031.818 | 1031.818
72 | 1027.675 | 1027.675
74 | 1023.844 | 1023.844
76 | 1020.888 | 1020.888
78 | 1023.648 | 1023.648
80 | 1027.566 | 1027.566
82 | 1032.371 | 1032.371
84 | 1034.983 | 1034.983
86 | 1033.213 | 1033.213
88 | 1031.188 | 1031.188
90 | 1029.08 | 1029.08
92 | 1026.322 | 1026.322
94 | 1023.207 | 1023.207
96 | 1021.503 | 1021.503
98 | 1019.765 | 1019.765
100 | 1018.493 | 1018.493
102 | 1016.444 | 1016.444
104 | 1013.288 | 1013.288
106 | 1007.843 | 1007.843
108 | 1001.282 | 1001.282
110 | 996.609 | 996.609
112 | 992.999 | 992.999
114 | 993.639 | 993.639
116 | 994.611 | 994.611
118 | 995.751 | 995.751
120 | 996.479 | 996.479
122 | 996.147 | 996.147
124 | 992.094 | 992.094
126 | 985.623 | 985.623
128 | 977.759 | 977.759
130 | 969.772 | 969.772
132 | 981.785 | 981.785
134 | 991.458 | 991.458
136 | 987.77 | 987.77
138 | 982.725 | 982.725
140 | 977.559 | 977.559
142 | 975.289 | 975.289
144 | 973.968 | 973.968
146 | 962.473 | 962.473
148 | 951.285 | 951.285
150 | 948.174 | 948.174
152 | 944.641 | 944.641
154 | 941.566 | 941.566
156 | 940.942 | 940.942
158 | 939.726 | 939.726
160 | 936.738 | 936.738
162 | 933.65 | 933.65
164 | 932.745 | 932.745
166 | 931.696 | 931.696
168 | 930.999 | 930.999
170 | 930.885 | 930.885
172 | 930.378 | 930.378
174 | 931.324 | 931.324
176 | 933.53 | 933.53
178 | 932.714 | 932.714
180 | 928.311 | 928.311
182 | 924.179 | 924.179
184 | 928.398 | 928.398
186 | 930.866 | 930.866
188 | 928.411 | 928.411
190 | 927.849 | 927.849
192 | 926.71 | 926.71
194 | 926.201 | 926.201
196 | 924.509 | 924.509
198 | 923.417 | 923.417
200 | 923.011 | 923.011
202 | 921.969 | 921.969
204 | 920.661 | 920.661
206 | 920.243 | 920.243
208 | 919.297 | 919.297
210 | 917.533 | 917.533
212 | 917.684 | 917.684
214 | 915.724 | 915.724
216 | 915.73 | 915.73
218 | 915.584 | 915.584
220 | 915.444 | 915.444
222 | 913.52 | 913.52
224 | 912.524 | 912.524
226 | 912.565 | 912.565
228 | 913.484 | 913.484
230 | 913.545 | 913.545
232 | 914.546 | 914.546
234 | 918.285 | 918.285
236 | 919.357 | 919.357
238 | 918.649 | 918.649
240 | 922.974 | 922.974
242 | 927.375 | 927.375
244 | 929.253 | 929.253
246 | 930.863 | 930.863
248 | 931.924 | 931.924
250 | 936.722 | 936.722
252 | 941.777 | 941.777
254 | 948.143 | 948.143
256 | 955.417 | 955.417
258 | 962.7 | 962.7
260 | 969.281 | 969.281
262 | 980.284 | 980.284
264 | 986.551 | 986.551
266 | 989.198 | 989.198
268 | 994.39 | 994.39
270 | 999.917 | 999.917
272 | 1004.623 | 1004.623
274 | 1008.819 | 1008.819
276 | 1007.834 | 1007.834
278 | 1005.626 | 1005.626
280 | 1001.623 | 1001.623
282 | 1004.052 | 1004.052
284 | 1010.797 | 1010.797
286 | 1014.67 | 1014.67
288 | 1017.319 | 1017.319
290 | 1027.459 | 1027.459
292 | 1031.99 | 1031.99
294 | 1036.254 | 1036.254
296 | 1040.127 | 1040.127
298 | 1044.396 | 1044.396
300 | 1051.339 | 1051.339
302 | 1060.955 | 1060.955
304 | 1070.227 | 1070.227
306 | 1072.691 | 1072.691
308 | 1076.503 | 1076.503
310 | 1083.996 | 1083.996
312 | 1097.188 | 1097.188
314 | 1103.545 | 1103.545
316 | 1105.174 | 1105.174
318 | 1111.657 | 1111.657
320 | 1122.935 | 1122.935
322 | 1128.197 | 1128.197
324 | 1132.561 | 1132.561
326 | 1131.854 | 1131.854
328 | 1133.338 | 1133.338
330 | 1136.405 | 1136.405
332 | 1128.709 | 1128.709
334 | 1120.713 | 1120.713
336 | 1115.226 | 1115.226
338 | 1108.709 | 1108.709
340 | 1102.499 | 1102.499
342 | 1096.349 | 1096.349
344 | 1090.39 | 1090.39
346 | 1087.765 | 1087.765
348 | 1084.661 | 1084.661
350 | 1081.662 | 1081.662
352 | 1076.872 | 1076.872
354 | 1070.898 | 1070.898
356 | 1065.018 | 1065.018
358 | 1059.58 | 1059.58
360 | 1055.284 | 1055.284
362 | 1050.886 | 1050.886
364 | 1052.647 | 1052.647
366 | 1051.117 | 1051.117
368 | 1048.266 | 1048.266
370 | 1040.172 | 1040.172
372 | 1033.483 | 1033.483
374 | 1030.95 | 1030.95
376 | 1032.263 | 1032.263
378 | 1031.391 | 1031.391
380 | 1025.791 | 1025.791
382 | 1020.911 | 1020.911
384 | 1015.65 | 1015.65
386 | 1012.139 | 1012.139
388 | 1010.472 | 1010.472
390 | 1005.401 | 1005.401
392 | 996.666 | 996.666
394 | 991.35 | 991.35
396 | 990.486 | 990.486
398 | 992.761 | 992.761
400 | 999.077 | 999.077
402 | 1001.8 | 1001.8
404 | 1002.224 | 1002.224
406 | 1002.003 | 1002.003
408 | 1003.596 | 1003.596
410 | 994.111 | 994.111
412 | 983.925 | 983.925
414 | 972.347 | 972.347
416 | 963.901 | 963.901
418 | 963.258 | 963.258
420 | 965.836 | 965.872
422 | 966.309 | 966.177
424 | 972.884 | 973.825
426 | 983.972 | 983.972
428 | 994.096 | 994.096
430 | 991.695 | 991.695
432 | 984.933 | 984.933
434 | 978.185 | 974.509
436 | 972.686 | 966.698
438 | 966.824 | 963.618
440 | 960.902 | 957.803
442 | 952.924 | 954.277
444 | 945.683 | 947.182
446 | 941.042 | 938.045
448 | 937.104 | 930.871
450 | 939.943 | 926.391
452 | 944.776 | 918.344
454 | 947.762 | 911.505
456 | 952.649 | 903.61
458 | 954.554 | 900.63
460 | 952.37 | 904.066
462 | 947.552 | 915.092
464 | 941.898 | 905.556
466 | 940.521 | 905.271
468 | 939.702 | 901.918
470 | 937.147 | 895.651
472 | 933.872 | 892.304
474 | 933.184 | 895.279
476 | 939.292 | 896.818
478 | 944.619 | 909.921
480 | 954.023 | 926.295
482 | 968.263 | 924.888
484 | 970.384 | 919.044
486 | 964.636 | 911.164
488 | 956.631 | 903.893
490 | 947.426 | 901.953
492 | 941.72 | 900.198
494 | 935.985 | 904.177
496 | 930.475 | 912.253
498 | 927.611 | 915.297
500 | 931.256 | 919.629
502 | 920.044
504 | 911.78
506 | 907.989
508 | 907.289
510 | 900.577
512 | 902.112
514 | 900.179
516 | 903.811
518 | 910.027
520 | 911.131 |  | End

## Profile data
Longitudinal profile data - Botswana pipeline
| OPTION 1: Pipeline goes through Serule before joining to BPT1 | OPTION2: Pipeline goes directly to BPT1
CHAINAGE (km0 | NGL (m) | NGL (m) |  | Botswana 1
2 | 1069.018 | 1069.018 | Start | Botswana 2
4 | 1067.321 | 1067.321
6 | 1064.035 | 1064.035
8 | 1063.832 | 1063.832
10 | 1067.893 | 1067.893
12 | 1075.133 | 1075.133
14 | 1082.768 | 1082.768
16 | 1089.726 | 1089.726
18 | 1094.131 | 1094.131
20 | 1097.897 | 1097.897
22 | 1101.67 | 1101.67
24 | 1095.952 | 1095.952
26 | 1090.107 | 1090.107
28 | 1085.781 | 1085.781
30 | 1081.89 | 1081.89
32 | 1077.937 | 1077.937
34 | 1074.89 | 1074.89
36 | 1071.114 | 1071.114
38 | 1065.311 | 1065.311
40 | 1059.051 | 1059.051
42 | 1054.28 | 1054.28
44 | 1053.871 | 1053.871
46 | 1050.42 | 1050.42
48 | 1052.704 | 1052.704
50 | 1056.355 | 1056.355
52 | 1058.466 | 1058.466
54 | 1055.99 | 1055.99
56 | 1055.66 | 1055.66
58 | 1056.404 | 1056.404
60 | 1056.841 | 1056.841
62 | 1056.377 | 1056.377
64 | 1052.503 | 1052.503
66 | 1046.022 | 1046.022
68 | 1036.575 | 1036.575
70 | 1031.818 | 1031.818
72 | 1027.675 | 1027.675
74 | 1023.844 | 1023.844
76 | 1020.888 | 1020.888
78 | 1023.648 | 1023.648
80 | 1027.566 | 1027.566
82 | 1032.371 | 1032.371
84 | 1034.983 | 1034.983
86 | 1033.213 | 1033.213
88 | 1031.188 | 1031.188
90 | 1029.08 | 1029.08
92 | 1026.322 | 1026.322
94 | 1023.207 | 1023.207
96 | 1021.503 | 1021.503
98 | 1019.765 | 1019.765
100 | 1018.493 | 1018.493
102 | 1016.444 | 1016.444
104 | 1013.288 | 1013.288
106 | 1007.843 | 1007.843
108 | 1001.282 | 1001.282
110 | 996.609 | 996.609
112 | 992.999 | 992.999
114 | 993.639 | 993.639
116 | 994.611 | 994.611
118 | 995.751 | 995.751
120 | 996.479 | 996.479
122 | 996.147 | 996.147
124 | 992.094 | 992.094
126 | 985.623 | 985.623
128 | 977.759 | 977.759
130 | 969.772 | 969.772
132 | 981.785 | 981.785
134 | 991.458 | 991.458
136 | 987.77 | 987.77
138 | 982.725 | 982.725
140 | 977.559 | 977.559
142 | 975.289 | 975.289
144 | 973.968 | 973.968
146 | 962.473 | 962.473
148 | 951.285 | 951.285
150 | 948.174 | 948.174
152 | 944.641 | 944.641
154 | 941.566 | 941.566
156 | 940.942 | 940.942
158 | 939.726 | 939.726
160 | 936.738 | 936.738
162 | 933.65 | 933.65
164 | 932.745 | 932.745
166 | 931.696 | 931.696
168 | 930.999 | 930.999
170 | 930.885 | 930.885
172 | 930.378 | 930.378
174 | 931.324 | 931.324
176 | 933.53 | 933.53
178 | 932.714 | 932.714
180 | 928.311 | 928.311
182 | 924.179 | 924.179
184 | 928.398 | 928.398
186 | 930.866 | 930.866
188 | 928.411 | 928.411
190 | 927.849 | 927.849
192 | 926.71 | 926.71
194 | 926.201 | 926.201
196 | 924.509 | 924.509
198 | 923.417 | 923.417
200 | 923.011 | 923.011
202 | 921.969 | 921.969
204 | 920.661 | 920.661
206 | 920.243 | 920.243
208 | 919.297 | 919.297
210 | 917.533 | 917.533
212 | 917.684 | 917.684
214 | 915.724 | 915.724
216 | 915.73 | 915.73
218 | 915.584 | 915.584
220 | 915.444 | 915.444
222 | 913.52 | 913.52
224 | 912.524 | 912.524
226 | 912.565 | 912.565
228 | 913.484 | 913.484
230 | 913.545 | 913.545
232 | 914.546 | 914.546
234 | 918.285 | 918.285
236 | 919.357 | 919.357
238 | 918.649 | 918.649
240 | 922.974 | 922.974
242 | 927.375 | 927.375
244 | 929.253 | 929.253
246 | 930.863 | 930.863
248 | 931.924 | 931.924
250 | 936.722 | 936.722
252 | 941.777 | 941.777
254 | 948.143 | 948.143
256 | 955.417 | 955.417
258 | 962.7 | 962.7
260 | 969.281 | 969.281
262 | 980.284 | 980.284
264 | 986.551 | 986.551
266 | 989.198 | 989.198
268 | 994.39 | 994.39
270 | 999.917 | 999.917
272 | 1004.623 | 1004.623
274 | 1008.819 | 1008.819
276 | 1007.834 | 1007.834
278 | 1005.626 | 1005.626
280 | 1001.623 | 1001.623
282 | 1004.052 | 1004.052
284 | 1010.797 | 1010.797
286 | 1014.67 | 1014.67
288 | 1017.319 | 1017.319
290 | 1027.459 | 1027.459
292 | 1031.99 | 1031.99
294 | 1036.254 | 1036.254
296 | 1040.127 | 1040.127
298 | 1044.396 | 1044.396
300 | 1051.339 | 1051.339
302 | 1060.955 | 1060.955
304 | 1070.227 | 1070.227
306 | 1072.691 | 1072.691
308 | 1076.503 | 1076.503
310 | 1083.996 | 1083.996
312 | 1097.188 | 1097.188
314 | 1103.545 | 1103.545
316 | 1105.174 | 1105.174
318 | 1111.657 | 1111.657
320 | 1122.935 | 1122.935
322 | 1128.197 | 1128.197
324 | 1132.561 | 1132.561
326 | 1131.854 | 1131.854
328 | 1133.338 | 1133.338
330 | 1136.405 | 1136.405
332 | 1128.709 | 1128.709
334 | 1120.713 | 1120.713
336 | 1115.226 | 1115.226
338 | 1108.709 | 1108.709
340 | 1102.499 | 1102.499
342 | 1096.349 | 1096.349
344 | 1090.39 | 1090.39
346 | 1087.765 | 1087.765
348 | 1084.661 | 1084.661
350 | 1081.662 | 1081.662
352 | 1076.872 | 1076.872
354 | 1070.898 | 1070.898
356 | 1065.018 | 1065.018
358 | 1059.58 | 1059.58
360 | 1055.284 | 1055.284
362 | 1050.886 | 1050.886
364 | 1052.647 | 1052.647
366 | 1051.117 | 1051.117
368 | 1048.266 | 1048.266
370 | 1040.172 | 1040.172
372 | 1033.483 | 1033.483
374 | 1030.95 | 1030.95
376 | 1032.263 | 1032.263
378 | 1031.391 | 1031.391
380 | 1025.791 | 1025.791
382 | 1020.911 | 1020.911
384 | 1015.65 | 1015.65
386 | 1012.139 | 1012.139
388 | 1010.472 | 1010.472
390 | 1005.401 | 1005.401
392 | 996.666 | 996.666
394 | 991.35 | 991.35
396 | 990.486 | 990.486
398 | 992.761 | 992.761
400 | 999.077 | 999.077
402 | 1001.8 | 1001.8
404 | 1002.224 | 1002.224
406 | 1002.003 | 1002.003
408 | 1003.596 | 1003.596
410 | 994.111 | 994.111
412 | 983.925 | 983.925
414 | 972.347 | 972.347
416 | 963.901 | 963.901
418 | 963.258 | 963.258
420 | 965.836 | 965.872
422 | 966.309 | 966.177
424 | 972.884 | 973.825
426 | 983.972 | 983.972
428 | 994.096 | 994.096
430 | 991.695 | 991.695
432 | 984.933 | 984.933
434 | 978.185 | 974.509
436 | 972.686 | 966.698
438 | 966.824 | 963.618
440 | 960.902 | 957.803
442 | 952.924 | 954.277
444 | 945.683 | 947.182
446 | 941.042 | 938.045
448 | 937.104 | 930.871
450 | 939.943 | 926.391
452 | 944.776 | 918.344
454 | 947.762 | 911.505
456 | 952.649 | 903.61
458 | 954.554 | 900.63
460 | 952.37 | 904.066
462 | 947.552 | 915.092
464 | 941.898 | 905.556
466 | 940.521 | 905.271
468 | 939.702 | 901.918
470 | 937.147 | 895.651
472 | 933.872 | 892.304
474 | 933.184 | 895.279
476 | 939.292 | 896.818
478 | 944.619 | 909.921
480 | 954.023 | 926.295
482 | 968.263 | 924.888
484 | 970.384 | 919.044
486 | 964.636 | 911.164
488 | 956.631 | 903.893
490 | 947.426 | 901.953
492 | 941.72 | 900.198
494 | 935.985 | 904.177
496 | 930.475 | 912.253
498 | 927.611 | 915.297
500 | 931.256 | 919.629
502 | 920.044
504 | 911.78
506 | 907.989
508 | 907.289
510 | 900.577
512 | 902.112
514 | 900.179
516 | 903.811
518 | 910.027
520 | 911.131 |  | End

## Flow Rate Calculations
Estimated Transfer Rate Demand | 100 | Mm3/a
Availible Days | 365
Pumping Hours | 24
Pf | 1.052
Pl | 1.02
PR | 1.2
Peak Design Flow | 4.0831 | m3/s

## Calculation Constants
Friction Factors
Ks (mm) - New | 0.03
Ks (mm) - Average | 0.06
Ks (mm) - Old | 0.15
Ks (mm) - Biofilm | 0.5
Kinemeatic Viscosity | 1.13e-06 | m2/s
Minor Loss - k | 150
Grade of Steel | X42
Yeild Capacity | 300 | Mpa
Design % of Yeild | 50%
Minimum D/t ratio | 160 | mm/mm

## Hydraulics
Option 1A |  |  |  | Option 1A | [12 empty] | Option 1A
Pump Station |  |  |  | Pipe Line | [9 empty] | Steel Pipeline Design |  |  | New Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Average Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Old Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes | [6 empty] | Biofilm Pipe Hydraulics - Darcy Weisbach & Karmen Prandtl Rough Pipes
Name | Chainage (km) | Elevation (m) | Pumped Head (m) | Reference | Chainage (km) | Elevation (m) | Section Length (km) | Diameter (m) | Flow Rate (m3/s) | PipeVelocity (m/s) | Re | Static Head (m) | Dynamic Head (m) | Design Pressure (m) | Pipe Wall thickness (mm) | Steel Mass (kg) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m) | λ | Hf (m) | Hl (m) | Htotal (m) | Pumping Head (m) | Dynamic Head (m) | HGL (m)
PS 1 | 8 | 1063.832 | 200 | Reservoir | 2 | 1069.018 | 0 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 10 | 10 | 10 | 13.75 | 0 | 0.008468 |  |  | 0 | 0 | 10 | 1079.018 | 0.0094904 |  |  | 0 | 0 | 10 | 1079.018 | 0.011153 |  |  | 0 | 0 | 10 | 1079.018 | 0.014105 |  |  | 0 | 0 | 10 | 1079.018
[5 empty] | 4 | 1067.321 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 11.697 | 11.2104 | 11.697 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 11.2104 | 1078.5314 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 11.1557 | 1078.4767 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 11.0669 | 1078.3879 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 10.9063 | 1078.2273
[5 empty] | 6 | 1064.035 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | 14.983 | 14.0098 | 14.983 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 14.0098 | 1078.0448 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 13.9005 | 1077.9355 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 13.7227 | 1077.7577 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 13.4016 | 1077.4366
|  |  |  | Pump Station | 8 | 1063.832 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 213.7262 | 213.5622 | 15.6612 | 1687311.5978 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 200 | 213.7262 | 1277.5582 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 200 | 213.5622 | 1277.3942 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 200 | 213.2956 | 1277.1276 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 200 | 212.8139 | 1276.6459
[5 empty] | 10 | 1067.893 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 209.1785 | 208.9599 | 15.3237 | 1651205.0538 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 209.1785 | 1277.0715 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 208.9599 | 1276.8529 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 208.6044 | 1276.4974 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 207.9622 | 1275.8552
Reservoirs |  |  |  |  | 12 | 1075.133 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 201.4519 | 201.1786 | 14.7531 | 1590132.5144 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 201.4519 | 1276.5849 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 201.1786 | 1276.3116 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 200.7343 | 1275.8673 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 199.9315 | 1275.0645
Name | Chainage (km) | Water Elevation (m) | Height |  | 14 | 1082.768 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 193.3303 | 193.0024 | 14.1535 | 1525925.148 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 193.3303 | 1276.0983 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 193.0024 | 1275.7704 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 192.4691 | 1275.2371 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 191.5058 | 1274.2738
Supply Resrvoir | 2 | 1079.018 | 10 |  | 16 | 1089.726 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 185.8857 | 185.5031 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 185.8857 | 1275.6117 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 185.5031 | 1275.2291 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 184.881 | 1274.607 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 183.7572 | 1273.4832
BPT 1 | 520 | 921.131 | 10 |  | 18 | 1094.131 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 180.9941 | 180.5568 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 180.9941 | 1275.1251 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 180.5568 | 1274.6878 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 179.8459 | 1273.9769 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 178.5615 | 1272.6925
[5 empty] | 20 | 1097.897 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 176.7415 | 176.2495 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 176.7415 | 1274.6385 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 176.2495 | 1274.1465 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 175.4497 | 1273.3467 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 174.0048 | 1271.9018
[5 empty] | 22 | 1101.67 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 172.4819 | 171.9353 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 172.4819 | 1274.1519 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 171.9353 | 1273.6053 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 171.0466 | 1272.7166 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 169.4411 | 1271.1111
[5 empty] | 24 | 1095.952 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 177.7132 | 177.112 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 177.7132 | 1273.6652 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 177.112 | 1273.064 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 176.1344 | 1272.0864 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 174.3684 | 1270.3204
[5 empty] | 26 | 1090.107 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 183.0716 | 182.4157 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 183.0716 | 1273.1786 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 182.4157 | 1272.5227 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 181.3493 | 1271.4563 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 179.4227 | 1269.5297
[5 empty] | 28 | 1085.781 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 186.911 | 186.2004 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 186.911 | 1272.692 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 186.2004 | 1271.9814 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 185.0451 | 1270.8261 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 182.958 | 1268.739
[5 empty] | 30 | 1081.89 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 190.3154 | 189.5502 | 13.9003 | 1498804.8635 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 190.3154 | 1272.2054 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 189.5502 | 1271.4402 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 188.306 | 1270.196 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 186.0583 | 1267.9483
[5 empty] | 32 | 1077.937 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 193.7818 | 192.9619 | 14.1505 | 1525607.3343 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 193.7818 | 1271.7188 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 192.9619 | 1270.8989 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 191.6289 | 1269.5659 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 189.2206 | 1267.1576
[5 empty] | 34 | 1074.89 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 196.3422 | 195.4676 | 14.3343 | 1545288.3505 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 196.3422 | 1271.2322 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 195.4676 | 1270.3576 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 194.0457 | 1268.9357 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 191.4769 | 1266.3669
[5 empty] | 36 | 1071.114 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 199.6316 | 198.7024 | 14.5715 | 1570690.3096 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 199.6316 | 1270.7456 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 198.7024 | 1269.8164 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 197.1916 | 1268.3056 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 194.4622 | 1265.5762
Route | Botswana 1 |  |  |  | 38 | 1065.311 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 204.948 | 203.9641 | 14.9574 | 1611998.2223 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 204.948 | 1270.259 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 203.9641 | 1269.2751 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 202.3644 | 1267.6754 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 199.4745 | 1264.7855
Option | 1 |  |  |  | 40 | 1059.051 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 210.7213 | 209.6828 | 15.3767 | 1656877.2207 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 210.7213 | 1269.7723 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 209.6828 | 1268.7338 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 207.9943 | 1267.0453 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 204.9438 | 1263.9948
[5 empty] | 42 | 1054.28 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 215.0057 | 213.9125 | 15.6869 | 1690059.7941 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 215.0057 | 1269.2857 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 213.9125 | 1268.1925 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 212.1351 | 1266.4151 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 208.9242 | 1263.2042
[5 empty] | 44 | 1053.871 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 214.9281 | 213.7803 | 15.6772 | 1689022.2423 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 214.9281 | 1268.7991 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 213.7803 | 1267.6513 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 211.914 | 1265.785 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 208.5425 | 1262.4135
[5 empty] | 46 | 1050.42 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 217.8925 | 216.69 | 15.8906 | 1711843.995 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 217.8925 | 1268.3125 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 216.69 | 1267.11 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 214.7349 | 1265.1549 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 211.2028 | 1261.6228
[5 empty] | 48 | 1052.704 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 215.1219 | 213.8647 | 15.6834 | 1689684.6959 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 215.1219 | 1267.8259 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 213.8647 | 1266.5687 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 211.8207 | 1264.5247 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 208.1281 | 1260.8321
[5 empty] | 50 | 1056.355 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 210.9843 | 209.6724 | 15.376 | 1656795.883 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 210.9843 | 1267.3393 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 209.6724 | 1266.0274 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 207.5396 | 1263.8946 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 203.6864 | 1260.0414
[5 empty] | 52 | 1058.466 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 208.3867 | 207.0202 | 15.1815 | 1635983.7124 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 208.3867 | 1266.8527 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 207.0202 | 1265.4862 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 204.7984 | 1263.2644 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 200.7847 | 1259.2507
[5 empty] | 54 | 1055.99 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 210.376 | 208.9549 | 15.3234 | 1651165.722 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 210.376 | 1266.366 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 208.9549 | 1264.9449 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 206.6443 | 1262.6343 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 202.47 | 1258.46
[5 empty] | 56 | 1055.66 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 210.2194 | 208.7436 | 15.3079 | 1649507.9342 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 210.2194 | 1265.8794 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 208.7436 | 1264.4036 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 206.3441 | 1262.0041 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 202.0093 | 1257.6693
[5 empty] | 58 | 1056.404 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 208.9888 | 207.4583 | 15.2136 | 1639422.333 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 208.9888 | 1265.3928 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 207.4583 | 1263.8623 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 204.97 | 1261.374 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 200.4746 | 1256.8786
[5 empty] | 60 | 1056.841 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 208.0652 | 206.4801 | 15.1419 | 1631745.1881 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 208.0652 | 1264.9062 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 206.4801 | 1263.3211 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 203.9028 | 1260.7438 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 199.2469 | 1256.0879
[5 empty] | 62 | 1056.377 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 208.0426 | 206.4028 | 15.1362 | 1631138.7528 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 208.0426 | 1264.4196 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 206.4028 | 1262.7798 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 203.7367 | 1260.1137 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 198.9202 | 1255.2972
[5 empty] | 64 | 1052.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 211.43 | 209.7355 | 15.3806 | 1657290.8753 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 211.43 | 1263.933 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 209.7355 | 1262.2385 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 206.9806 | 1259.4836 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 202.0035 | 1254.5065
[5 empty] | 66 | 1046.022 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 217.4244 | 215.6753 | 15.8162 | 1703885.687 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 217.4244 | 1263.4464 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 215.6753 | 1261.6973 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 212.8314 | 1258.8534 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 207.6938 | 1253.7158
[5 empty] | 68 | 1036.575 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 226.3847 | 224.581 | 16.4693 | 1773712.5297 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 226.3847 | 1262.9597 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 224.581 | 1261.156 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 221.6483 | 1258.2233 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 216.3502 | 1252.9252
[5 empty] | 70 | 1031.818 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 230.6551 | 228.7967 | 16.7784 | 1806751.9689 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 230.6551 | 1262.4731 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 228.7967 | 1260.6147 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 225.7751 | 1257.5931 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 220.3165 | 1252.1345
[5 empty] | 72 | 1027.675 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 234.3115 | 232.3984 | 17.0426 | 1834971.9067 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 234.3115 | 1261.9865 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 232.3984 | 1260.0734 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 229.288 | 1256.963 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 223.6688 | 1251.3438
[5 empty] | 74 | 1023.844 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 237.6559 | 235.6882 | 17.2838 | 1860741.2756 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 237.6559 | 1261.4999 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 235.6882 | 1259.5322 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 232.4888 | 1256.3328 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 226.7091 | 1250.5531
[5 empty] | 76 | 1020.888 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 240.1253 | 238.1029 | 17.4609 | 1879652.8659 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 240.1253 | 1261.0133 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 238.1029 | 1258.9909 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 234.8147 | 1255.7027 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 228.8744 | 1249.7624
[5 empty] | 78 | 1023.648 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 236.8787 | 234.8016 | 17.2188 | 1853797.268 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 236.8787 | 1260.5267 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 234.8016 | 1258.4496 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 231.4246 | 1255.0726 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 225.3237 | 1248.9717
[5 empty] | 80 | 1027.566 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 232.4741 | 230.3423 | 16.8918 | 1818863.0259 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 232.4741 | 1260.0401 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 230.3423 | 1257.9083 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 226.8764 | 1254.4424 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 220.615 | 1248.181
[5 empty] | 82 | 1032.371 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 227.1824 | 224.9961 | 16.4997 | 1776966.0619 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 227.1824 | 1259.5534 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 224.9961 | 1257.3671 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 221.4413 | 1253.8123 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 215.0193 | 1247.3903
[5 empty] | 84 | 1034.983 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 224.0838 | 221.8428 | 16.2685 | 1752247.7998 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 224.0838 | 1259.0668 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 221.8428 | 1256.8258 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 218.1991 | 1253.1821 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 211.6166 | 1246.5996
[5 empty] | 86 | 1033.213 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 225.3672 | 223.0715 | 16.3586 | 1761880.3193 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 225.3672 | 1258.5802 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 223.0715 | 1256.2845 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 219.339 | 1252.552 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 212.5959 | 1245.8089
[5 empty] | 88 | 1031.188 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 226.9056 | 224.5552 | 16.4674 | 1773510.8264 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 226.9056 | 1258.0936 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 224.5552 | 1255.7432 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 220.7338 | 1251.9218 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 213.8302 | 1245.0182
[5 empty] | 90 | 1029.08 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 228.527 | 226.122 | 16.5823 | 1785790.6791 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 228.527 | 1257.607 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 226.122 | 1255.202 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 222.2117 | 1251.2917 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 215.1475 | 1244.2275
[5 empty] | 92 | 1026.322 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 230.7984 | 228.3387 | 16.7448 | 1803162.9443 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 230.7984 | 1257.1204 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 228.3387 | 1254.6607 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 224.3396 | 1250.6616 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 217.1148 | 1243.4368
[5 empty] | 94 | 1023.207 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 233.4268 | 230.9124 | 16.9336 | 1823329.7125 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 233.4268 | 1256.6338 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 230.9124 | 1254.1194 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 226.8244 | 1250.0314 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 219.4392 | 1242.6462
[5 empty] | 96 | 1021.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 234.6441 | 232.0752 | 17.0188 | 1832439.2554 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 234.6441 | 1256.1471 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 232.0752 | 1253.5782 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 227.8983 | 1249.4013 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 220.3525 | 1241.8555
[5 empty] | 98 | 1019.765 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 235.8955 | 233.2719 | 17.1066 | 1841814.4271 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 235.8955 | 1255.6605 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 233.2719 | 1253.0369 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 229.0061 | 1248.7711 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 221.2998 | 1241.0648
[5 empty] | 100 | 1018.493 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 236.6809 | 234.0026 | 17.1602 | 1847538.5755 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 236.6809 | 1255.1739 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 234.0026 | 1252.4956 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 229.648 | 1248.141 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 221.7811 | 1240.2741
[5 empty] | 102 | 1016.444 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 238.2433 | 235.5103 | 17.2708 | 1859348.459 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 238.2433 | 1254.6873 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 235.5103 | 1251.9543 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 231.0668 | 1247.5108 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 223.0394 | 1239.4834
[5 empty] | 104 | 1013.288 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 240.9127 | 238.1251 | 17.4625 | 1879826.5117 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 240.9127 | 1254.2007 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 238.1251 | 1251.4131 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 233.5927 | 1246.8807 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 225.4047 | 1238.6927
[5 empty] | 106 | 1007.843 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 245.8711 | 243.0288 | 17.8221 | 1918221.8071 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 245.8711 | 1253.7141 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 243.0288 | 1250.8718 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 238.4076 | 1246.2506 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 230.059 | 1237.902
[5 empty] | 108 | 1001.282 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 251.9455 | 249.0485 | 18.2636 | 1965337.7393 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 251.9455 | 1253.2275 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 249.0485 | 1250.3305 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 244.3384 | 1245.6204 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 235.8293 | 1237.1113
[5 empty] | 110 | 996.609 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 256.1319 | 253.1802 | 18.5666 | 1997665.3173 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 256.1319 | 1252.7409 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 253.1802 | 1249.7892 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 248.3813 | 1244.9903 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 239.7116 | 1236.3206
[5 empty] | 112 | 992.999 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 259.2552 | 256.249 | 18.7916 | 2021669.8783 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 259.2552 | 1252.2542 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 256.249 | 1249.248 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 251.3611 | 1244.3601 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 242.5309 | 1235.5299
[5 empty] | 114 | 993.639 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 258.1286 | 255.0677 | 18.705 | 2012430.1724 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 258.1286 | 1251.7676 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 255.0677 | 1248.7067 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 250.091 | 1243.73 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 241.1002 | 1234.7392
[5 empty] | 116 | 994.611 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 256.67 | 253.5544 | 18.594 | 2000592.541 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 256.67 | 1251.281 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 253.5544 | 1248.1654 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 248.4888 | 1243.0998 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 239.3375 | 1233.9485
[5 empty] | 118 | 995.751 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 255.0434 | 251.8731 | 18.4707 | 1987439.2994 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 255.0434 | 1250.7944 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 251.8731 | 1247.6241 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 246.7187 | 1242.4697 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 237.4068 | 1233.1578
[5 empty] | 120 | 996.479 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 253.8288 | 250.6039 | 18.3776 | 1977508.2974 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 253.8288 | 1250.3078 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 250.6039 | 1247.0829 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 245.3606 | 1241.8396 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 235.8882 | 1232.3672
[5 empty] | 122 | 996.147 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 253.6742 | 250.3946 | 18.3623 | 1975870.8268 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 253.6742 | 1249.8212 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 250.3946 | 1246.5416 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 245.0624 | 1241.2094 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 235.4295 | 1231.5765
[5 empty] | 124 | 992.094 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 257.2406 | 253.9063 | 18.6198 | 2003345.4522 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 257.2406 | 1249.3346 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 253.9063 | 1246.0003 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 248.4853 | 1240.5793 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 238.6918 | 1230.7858
[5 empty] | 126 | 985.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 263.2249 | 259.8361 | 19.0546 | 2049722.8856 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 263.2249 | 1248.8479 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 259.8361 | 1245.4591 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 254.3261 | 1239.9491 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 244.3721 | 1229.9951
[5 empty] | 128 | 977.759 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 270.6023 | 267.1588 | 19.5916 | 2106969.4757 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 270.6023 | 1248.3613 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 267.1588 | 1244.9178 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 261.56 | 1239.319 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 251.4454 | 1229.2044
[5 empty] | 130 | 969.772 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 278.1027 | 274.6045 | 20.1377 | 2165148.4709 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 278.1027 | 1247.8747 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 274.6045 | 1244.3765 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 268.9168 | 1238.6888 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 258.6417 | 1228.4137
[5 empty] | 132 | 981.785 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 265.6031 | 262.0502 | 19.217 | 2067035.5939 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 265.6031 | 1247.3881 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 262.0502 | 1243.8352 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 256.2737 | 1238.0587 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 245.838 | 1227.623
[5 empty] | 134 | 991.458 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 255.4435 | 251.836 | 18.468 | 1987148.3591 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 255.4435 | 1246.9015 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 251.836 | 1243.294 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 245.9706 | 1237.4286 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 235.3743 | 1226.8323
[5 empty] | 136 | 987.77 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 258.6449 | 254.9827 | 18.6987 | 2011765.24 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 258.6449 | 1246.4149 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 254.9827 | 1242.7527 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 249.0284 | 1236.7984 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 238.2716 | 1226.0416
[5 empty] | 138 | 982.725 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 263.2033 | 259.4864 | 19.029 | 2046988.8089 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 263.2033 | 1245.9283 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 259.4864 | 1242.2114 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 253.4433 | 1236.1683 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 242.5259 | 1225.2509
[5 empty] | 140 | 977.559 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 267.8826 | 264.1111 | 19.3682 | 2083147.5188 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 267.8826 | 1245.4416 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 264.1111 | 1241.6701 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 257.9791 | 1235.5381 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 246.9012 | 1224.4602
[5 empty] | 142 | 975.289 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 269.666 | 265.8399 | 19.4949 | 2096660.7615 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 269.666 | 1244.955 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 265.8399 | 1241.1289 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 259.619 | 1234.908 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 248.3805 | 1223.6695
[5 empty] | 144 | 973.968 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 270.5004 | 266.6196 | 19.5521 | 2102755.2698 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 270.5004 | 1244.4684 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 266.6196 | 1240.5876 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 260.3098 | 1234.2778 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 248.9108 | 1222.8788
[5 empty] | 146 | 962.473 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 281.5088 | 277.5733 | 20.3554 | 2188337.8163 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 281.5088 | 1243.9818 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 277.5733 | 1240.0463 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 271.1747 | 1233.6477 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 259.6151 | 1222.0881
[5 empty] | 148 | 951.285 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 292.2102 | 288.22 | 21.1361 | 2271460.7414 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 292.2102 | 1243.4952 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 288.22 | 1239.505 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 281.7326 | 1233.0176 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 270.0125 | 1221.2975
[5 empty] | 150 | 948.174 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 294.8346 | 290.7898 | 21.3246 | 2291514.5377 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 294.8346 | 1243.0086 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 290.7898 | 1238.9638 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 284.2134 | 1232.3874 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 272.3328 | 1220.5068
[5 empty] | 152 | 944.641 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 297.881 | 293.7815 | 21.544 | 2314857.1511 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 297.881 | 1242.522 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 293.7815 | 1238.4225 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 287.1163 | 1231.7573 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 275.0751 | 1219.7161
[5 empty] | 154 | 941.566 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 300.4693 | 296.3152 | 21.7298 | 2334622.5572 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 300.4693 | 1242.0353 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 296.3152 | 1237.8812 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 289.5611 | 1231.1271 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 277.3594 | 1218.9254
[5 empty] | 156 | 940.942 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 300.6067 | 296.398 | 21.7359 | 2335267.8444 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 300.6067 | 1241.5487 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 296.398 | 1237.34 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 289.555 | 1230.497 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 277.1927 | 1218.1347
[5 empty] | 158 | 939.726 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 301.3361 | 297.0727 | 21.7853 | 2340530.7314 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 301.3361 | 1241.0621 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 297.0727 | 1236.7987 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 290.1408 | 1229.8668 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 277.618 | 1217.344
[5 empty] | 160 | 936.738 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 303.8375 | 299.5194 | 21.9648 | 2359613.2418 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 303.8375 | 1240.5755 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 299.5194 | 1236.2574 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 292.4987 | 1229.2367 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 279.8153 | 1216.5533
[5 empty] | 162 | 933.65 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 306.4389 | 302.0661 | 22.1515 | 2379472.299 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 306.4389 | 1240.0889 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 302.0661 | 1235.7161 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 294.9566 | 1228.6066 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 282.1126 | 1215.7626
[5 empty] | 164 | 932.745 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 306.8573 | 302.4299 | 22.1782 | 2382308.3136 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 306.8573 | 1239.6023 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 302.4299 | 1235.1749 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 295.2314 | 1227.9764 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 282.2269 | 1214.9719
[5 empty] | 166 | 931.696 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.4197 | 302.9376 | 22.2154 | 2386266.9938 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 307.4197 | 1239.1157 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 302.9376 | 1234.6336 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 295.6503 | 1227.3463 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 282.4852 | 1214.1812
[5 empty] | 168 | 930.999 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.63 | 303.0933 | 22.2268 | 2387481.1476 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 307.63 | 1238.629 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 303.0933 | 1234.0923 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 295.7171 | 1226.7161 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 282.3915 | 1213.3905
[5 empty] | 170 | 930.885 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.2574 | 302.666 | 22.1955 | 2384149.7967 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 307.2574 | 1238.1424 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 302.666 | 1233.551 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 295.201 | 1226.086 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 281.7148 | 1212.5998
[5 empty] | 172 | 930.378 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.2778 | 302.6318 | 22.193 | 2383882.5715 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 307.2778 | 1237.6558 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 302.6318 | 1233.0098 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 295.0778 | 1225.4558 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 281.4311 | 1211.8091
[5 empty] | 174 | 931.324 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 305.8452 | 301.1445 | 22.0839 | 2372285.864 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 305.8452 | 1237.1692 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 301.1445 | 1232.4685 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 293.5017 | 1224.8257 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 279.6945 | 1211.0185
[5 empty] | 176 | 933.53 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 303.1526 | 298.3972 | 21.8825 | 2350861.4801 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 303.1526 | 1236.6826 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 298.3972 | 1231.9272 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 290.6655 | 1224.1955 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 276.6978 | 1210.2278
[5 empty] | 178 | 932.714 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 303.482 | 298.6719 | 21.9026 | 2353004.0937 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 303.482 | 1236.196 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 298.6719 | 1231.3859 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 290.8514 | 1223.5654 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 276.7231 | 1209.4371
[5 empty] | 180 | 928.311 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.3984 | 302.5337 | 22.1858 | 2383117.7461 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 307.3984 | 1235.7094 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 302.5337 | 1230.8447 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 294.6243 | 1222.9353 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 280.3354 | 1208.6464
[5 empty] | 182 | 924.179 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 311.0438 | 306.1244 | 22.4491 | 2411111.049 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 311.0438 | 1235.2228 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 306.1244 | 1230.3034 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 298.1261 | 1222.3051 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 283.6767 | 1207.8557
[5 empty] | 184 | 928.398 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 306.3381 | 301.3641 | 22.1 | 2373998.4849 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 306.3381 | 1234.7361 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 301.3641 | 1229.7621 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 293.277 | 1221.675 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 278.667 | 1207.065
[5 empty] | 186 | 930.866 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 303.3835 | 298.3549 | 21.8794 | 2350531.0571 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 303.3835 | 1234.2495 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 298.3549 | 1229.2209 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 290.1788 | 1221.0448 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 275.4083 | 1206.2743
[5 empty] | 188 | 928.411 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 305.3519 | 300.2686 | 22.0197 | 2365455.5628 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 305.3519 | 1233.7629 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 300.2686 | 1228.6796 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 292.0037 | 1220.4147 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 277.0726 | 1205.4836
[5 empty] | 190 | 927.849 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 305.4273 | 300.2893 | 22.0212 | 2365617.1927 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 305.4273 | 1233.2763 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 300.2893 | 1228.1383 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 291.9355 | 1219.7845 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 276.8439 | 1204.6929
[5 empty] | 192 | 926.71 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 306.0797 | 300.887 | 22.065 | 2370278.2559 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 306.0797 | 1232.7897 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 300.887 | 1227.597 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 292.4444 | 1219.1544 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 277.1922 | 1203.9022
[5 empty] | 194 | 926.201 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 306.1021 | 300.8548 | 22.0627 | 2370026.594 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 306.1021 | 1232.3031 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 300.8548 | 1227.0558 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 292.3233 | 1218.5243 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 276.9105 | 1203.1115
[5 empty] | 196 | 924.509 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.3075 | 302.0055 | 22.1471 | 2378999.4283 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 307.3075 | 1231.8165 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 302.0055 | 1226.5145 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 293.3851 | 1217.8941 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 277.8118 | 1202.3208
[5 empty] | 198 | 923.417 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.9128 | 302.5562 | 22.1875 | 2383293.4916 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 307.9128 | 1231.3298 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 302.5562 | 1225.9732 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 293.847 | 1217.264 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 278.1131 | 1201.5301
[5 empty] | 200 | 923.011 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 307.8322 | 302.4209 | 22.1775 | 2382238.769 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 307.8322 | 1230.8432 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 302.4209 | 1225.4319 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 293.6228 | 1216.6338 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 277.7285 | 1200.7395
[5 empty] | 202 | 921.969 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 308.3876 | 302.9217 | 22.2143 | 2386142.8744 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 308.3876 | 1230.3566 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 302.9217 | 1224.8907 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 294.0347 | 1216.0037 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 277.9798 | 1199.9488
[5 empty] | 204 | 920.661 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 309.209 | 303.6884 | 22.2705 | 2392120.6917 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 309.209 | 1229.87 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 303.6884 | 1224.3494 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 294.7125 | 1215.3735 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 278.4971 | 1199.1581
[5 empty] | 206 | 920.243 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 309.1404 | 303.5651 | 22.2614 | 2391159.6072 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 309.1404 | 1229.3834 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 303.5651 | 1223.8081 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 294.5004 | 1214.7434 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 278.1244 | 1198.3674
[5 empty] | 208 | 919.297 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 309.5998 | 303.9699 | 22.2911 | 2394314.9769 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 309.5998 | 1228.8968 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 303.9699 | 1223.2669 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 294.8163 | 1214.1133 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 278.2797 | 1197.5767
[5 empty] | 210 | 917.533 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 310.8772 | 305.1926 | 22.3808 | 2403847.1898 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 310.8772 | 1228.4102 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 305.1926 | 1222.7256 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 295.9501 | 1213.4831 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 279.253 | 1196.786
[5 empty] | 212 | 917.684 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 310.2395 | 304.5003 | 22.33 | 2398450.4177 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 310.2395 | 1227.9235 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 304.5003 | 1222.1843 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 295.169 | 1212.853 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 278.3113 | 1195.9953
[5 empty] | 214 | 915.724 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 311.7129 | 305.919 | 22.4341 | 2409510.1473 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 311.7129 | 1227.4369 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 305.919 | 1221.643 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 296.4988 | 1212.2228 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 279.4806 | 1195.2046
[5 empty] | 216 | 915.73 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 311.2203 | 305.3718 | 22.3939 | 2405243.9872 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 311.2203 | 1226.9503 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 305.3718 | 1221.1018 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 295.8627 | 1211.5927 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 278.6839 | 1194.4139
[5 empty] | 218 | 915.584 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 310.8797 | 304.9765 | 22.3649 | 2402162.614 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 310.8797 | 1226.4637 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 304.9765 | 1220.5605 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 295.3785 | 1210.9625 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 278.0392 | 1193.6232
[5 empty] | 220 | 915.444 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 310.5331 | 304.5752 | 22.3355 | 2399034.3827 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 310.5331 | 1225.9771 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 304.5752 | 1220.0192 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 294.8884 | 1210.3324 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 277.3885 | 1192.8325
[5 empty] | 222 | 913.52 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 311.9705 | 305.9579 | 22.4369 | 2409813.4314 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 311.9705 | 1225.4905 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 305.9579 | 1219.4779 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 296.1823 | 1209.7023 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 278.5218 | 1192.0418
[5 empty] | 224 | 912.524 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 312.4799 | 306.4127 | 22.4703 | 2413358.0327 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 312.4799 | 1225.0039 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 306.4127 | 1218.9367 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 296.5481 | 1209.0721 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 278.7271 | 1191.2511
[5 empty] | 226 | 912.565 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 311.9522 | 305.8304 | 22.4276 | 2408819.1841 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 311.9522 | 1224.5172 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 305.8304 | 1218.3954 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 295.877 | 1208.442 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 277.8955 | 1190.4605
[5 empty] | 228 | 913.484 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 310.5466 | 304.3701 | 22.3205 | 2397435.4919 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 310.5466 | 1224.0306 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 304.3701 | 1217.8541 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 294.3278 | 1207.8118 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 276.1858 | 1189.6698
[5 empty] | 230 | 913.545 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 309.999 | 303.7678 | 22.2763 | 2392740.0866 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 309.999 | 1223.544 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 303.7678 | 1217.3128 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 293.6367 | 1207.1817 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 275.3341 | 1188.8791
[5 empty] | 232 | 914.546 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 308.5114 | 302.2256 | 22.1632 | 2380715.4349 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 308.5114 | 1223.0574 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 302.2256 | 1216.7716 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 292.0055 | 1206.5515 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 273.5424 | 1188.0884
[5 empty] | 234 | 918.285 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 304.2858 | 297.9453 | 21.8493 | 2347336.7914 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 304.2858 | 1222.5708 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 297.9453 | 1216.2303 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 287.6364 | 1205.9214 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 269.0127 | 1187.2977
[5 empty] | 236 | 919.357 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 302.7272 | 296.332 | 21.731 | 2334753.5601 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 302.7272 | 1222.0842 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 296.332 | 1215.689 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 285.9343 | 1205.2913 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 267.15 | 1186.507
[5 empty] | 238 | 918.649 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 302.9486 | 296.4988 | 21.7432 | 2336054.0612 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 302.9486 | 1221.5976 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 296.4988 | 1215.1478 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 286.0121 | 1204.6611 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 267.0673 | 1185.7163
[5 empty] | 240 | 922.974 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 298.1369 | 291.6325 | 21.3864 | 2298090.1025 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 298.1369 | 1221.1109 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 291.6325 | 1214.6065 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 281.057 | 1204.031 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 261.9516 | 1184.9256
[5 empty] | 242 | 927.375 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 293.2493 | 286.6902 | 21.0239 | 2259520.3757 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 293.2493 | 1220.6243 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 286.6902 | 1214.0652 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 276.0258 | 1203.4008 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 256.7599 | 1184.1349
[5 empty] | 244 | 929.253 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 290.8847 | 284.2709 | 20.8465 | 2240635.5322 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 290.8847 | 1220.1377 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 284.2709 | 1213.5239 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 273.5177 | 1202.7707 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 254.0912 | 1183.3442
[5 empty] | 246 | 930.863 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 288.7881 | 282.1197 | 20.6888 | 2223840.0883 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 288.7881 | 1219.6511 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 282.1197 | 1212.9827 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 271.2775 | 1202.1405 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 251.6905 | 1182.5535
[5 empty] | 248 | 931.924 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 287.2405 | 280.5174 | 20.5713 | 2211329.2078 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 287.2405 | 1219.1645 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 280.5174 | 1212.4414 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 269.5864 | 1201.5104 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 249.8388 | 1181.7628
[5 empty] | 250 | 936.722 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 281.9559 | 275.1781 | 20.1797 | 2169629.2295 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 281.9559 | 1218.6779 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 275.1781 | 1211.9001 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 264.1583 | 1200.8803 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 244.2501 | 1180.9721
[5 empty] | 252 | 941.777 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 276.4143 | 269.5818 | 19.7693 | 2125905.8362 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 276.4143 | 1218.1913 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 269.5818 | 1211.3588 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 258.4731 | 1200.2501 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 238.4045 | 1180.1815
[5 empty] | 254 | 948.143 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 269.5617 | 262.6746 | 19.2628 | 2071916.7596 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 269.5617 | 1217.7047 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 262.6746 | 1210.8176 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 251.477 | 1199.62 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 231.2478 | 1179.3908
[5 empty] | 256 | 955.417 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 261.801 | 254.8593 | 18.6897 | 2010799.995 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 261.801 | 1217.218 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 254.8593 | 1210.2763 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 243.5728 | 1198.9898 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 223.1831 | 1178.6001
[5 empty] | 258 | 962.7 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 254.0314 | 247.035 | 18.1159 | 1949580.3909 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 254.0314 | 1216.7314 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 247.035 | 1209.735 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 235.6597 | 1198.3597 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 215.1094 | 1177.8094
[5 empty] | 260 | 969.281 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 246.9638 | 239.9127 | 17.5936 | 1893825.2217 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 246.9638 | 1216.2448 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 239.9127 | 1209.1937 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 228.4485 | 1197.7295 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 207.7377 | 1177.0187
[5 empty] | 262 | 980.284 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 235.4742 | 228.3685 | 16.747 | 1803396.2273 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 235.4742 | 1215.7582 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 228.3685 | 1208.6525 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 216.8154 | 1197.0994 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 195.944 | 1176.228
[5 empty] | 264 | 986.551 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 228.7206 | 221.5602 | 16.2477 | 1750032.2867 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 228.7206 | 1215.2716 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 221.5602 | 1208.1112 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 209.9183 | 1196.4693 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 188.8863 | 1175.4373
[5 empty] | 266 | 989.198 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 225.587 | 218.3719 | 16.0139 | 1725033.8215 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 225.587 | 1214.785 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 218.3719 | 1207.5699 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 206.6411 | 1195.8391 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 185.4486 | 1174.6466
[5 empty] | 268 | 994.39 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 219.9084 | 212.6387 | 15.5935 | 1680067.071 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 219.9084 | 1214.2984 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 212.6387 | 1207.0287 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 200.819 | 1195.209 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 179.4659 | 1173.8559
[5 empty] | 270 | 999.917 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 213.8947 | 206.5704 | 15.1485 | 1632453.8797 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 213.8947 | 1213.8117 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 206.5704 | 1206.4874 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 194.6618 | 1194.5788 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 173.1482 | 1173.0652
[5 empty] | 272 | 1004.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 208.7021 | 201.3231 | 14.7637 | 1591266.7105 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 208.7021 | 1213.3251 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 201.3231 | 1205.9461 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 189.3257 | 1193.9487 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 167.6515 | 1172.2745
[5 empty] | 274 | 1008.819 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 204.0195 | 196.5858 | 14.4163 | 1554070.1136 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 204.0195 | 1212.8385 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 196.5858 | 1205.4048 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 184.4995 | 1193.3185 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 162.6648 | 1171.4838
[5 empty] | 276 | 1007.834 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 204.5179 | 197.0296 | 14.4488 | 1557554.7167 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 204.5179 | 1212.3519 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 197.0296 | 1204.8636 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 184.8544 | 1192.6884 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 162.8591 | 1170.6931
[5 empty] | 278 | 1005.626 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 206.2393 | 198.6963 | 14.5711 | 1570642.6534 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 206.2393 | 1211.8653 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 198.6963 | 1204.3223 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 186.4323 | 1192.0583 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 164.2765 | 1169.9025
[5 empty] | 280 | 1001.623 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 209.7557 | 202.158 | 14.8249 | 1597821.0813 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 209.7557 | 1211.3787 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 202.158 | 1203.781 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 189.8051 | 1191.4281 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 167.4888 | 1169.1118
[5 empty] | 282 | 1004.052 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 206.8401 | 199.1877 | 14.6071 | 1574501.4997 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 206.8401 | 1210.8921 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 199.1877 | 1203.2397 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 186.746 | 1190.798 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 164.2691 | 1168.3211
[5 empty] | 284 | 1010.797 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 199.6084 | 191.9015 | 14.0728 | 1517277.2291 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 199.6084 | 1210.4054 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 191.9015 | 1202.6985 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 179.3708 | 1190.1678 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 156.7334 | 1167.5304
[5 empty] | 286 | 1014.67 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 195.2488 | 187.4872 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 195.2488 | 1209.9188 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 187.4872 | 1202.1572 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 174.8677 | 1189.5377 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 152.0697 | 1166.7397
[5 empty] | 288 | 1017.319 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 192.1132 | 184.2969 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 192.1132 | 1209.4322 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 184.2969 | 1201.6159 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 171.5885 | 1188.9075 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 148.63 | 1165.949
[5 empty] | 290 | 1027.459 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 181.4866 | 173.6156 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 181.4866 | 1208.9456 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 173.6156 | 1201.0746 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 160.8184 | 1188.2774 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 137.6993 | 1165.1583
[5 empty] | 292 | 1031.99 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 176.469 | 168.5434 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 176.469 | 1208.459 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 168.5434 | 1200.5334 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 155.6572 | 1187.6472 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 132.3776 | 1164.3676
[5 empty] | 294 | 1036.254 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 171.7184 | 163.7381 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 171.7184 | 1207.9724 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 163.7381 | 1199.9921 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 150.7631 | 1187.0171 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 127.3229 | 1163.5769
[5 empty] | 296 | 1040.127 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 167.3588 | 159.3238 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 167.3588 | 1207.4858 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 159.3238 | 1199.4508 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 146.26 | 1186.387 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 122.6592 | 1162.7862
[5 empty] | 298 | 1044.396 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 162.6031 | 154.5136 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 162.6031 | 1206.9991 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 154.5136 | 1198.9096 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 141.3608 | 1185.7568 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 117.5995 | 1161.9955
[5 empty] | 300 | 1051.339 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 155.1735 | 147.0293 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 155.1735 | 1206.5125 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 147.0293 | 1198.3683 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 133.7877 | 1185.1267 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 109.8658 | 1161.2048
[5 empty] | 302 | 1060.955 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 145.0709 | 136.872 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 145.0709 | 1206.0259 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 136.872 | 1197.827 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 123.5415 | 1184.4965 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 99.4591 | 1160.4141
[5 empty] | 304 | 1070.227 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 135.3123 | 127.0587 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 135.3123 | 1205.5393 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 127.0587 | 1197.2857 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 113.6394 | 1183.8664 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 89.3965 | 1159.6235
[5 empty] | 306 | 1072.691 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 132.3617 | 124.0535 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 132.3617 | 1205.0527 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 124.0535 | 1196.7445 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 110.5452 | 1183.2362 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 86.1418 | 1158.8328
[5 empty] | 308 | 1076.503 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 128.0631 | 119.7002 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 128.0631 | 1204.5661 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 119.7002 | 1196.2032 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 106.1031 | 1182.6061 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 81.5391 | 1158.0421
[5 empty] | 310 | 1083.996 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 120.0835 | 111.6659 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 120.0835 | 1204.0795 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 111.6659 | 1195.6619 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 97.98 | 1181.976 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 73.2554 | 1157.2514
[5 empty] | 312 | 1097.188 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 106.4049 | 97.9326 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 106.4049 | 1203.5929 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 97.9326 | 1195.1206 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 84.1578 | 1181.3458 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 59.2727 | 1156.4607
[5 empty] | 314 | 1103.545 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 99.5612 | 91.0344 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 99.5612 | 1203.1062 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 91.0344 | 1194.5794 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 77.1707 | 1180.7157 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 52.125 | 1155.67
[5 empty] | 316 | 1105.174 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 97.4456 | 88.8641 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 97.4456 | 1202.6196 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 88.8641 | 1194.0381 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 74.9115 | 1180.0855 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 49.7053 | 1154.8793
[5 empty] | 318 | 1111.657 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 90.476 | 81.8398 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 90.476 | 1202.133 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 81.8398 | 1193.4968 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 67.7984 | 1179.4554 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 42.4316 | 1154.0886
[5 empty] | 320 | 1122.935 | 2 | 2.2 | 4.0831 | 1.0741 | 2091219.1393 | Greater Dynamic Pressures | 78.7114 | 70.0205 | 13.75 | 1482695.7604 | 0.008468 | 0.45269 | 0.033926 | 0.48661 | 0 | 78.7114 | 1201.6464 | 0.0094904 | 0.50735 | 0.033926 | 0.54127 | 0 | 70.0205 | 1192.9555 | 0.011153 | 0.59622 | 0.033926 | 0.63014 | 0 | 55.8902 | 1178.8252 | 0.014105 | 0.75677 | 0.033926 | 0.79069 | 0 | 30.3629 | 1153.2979
[5 empty] | 322 | 1128.197 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 72.6594 | 63.8784 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 72.6594 | 1200.8564 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 63.8784 | 1192.0754 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 49.6013 | 1177.7983 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 23.8076 | 1152.0046
[5 empty] | 324 | 1132.561 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 67.5055 | 58.6343 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 67.5055 | 1200.0665 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 58.6343 | 1191.1953 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 44.2105 | 1176.7715 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 18.1503 | 1150.7113
[5 empty] | 326 | 1131.854 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 67.4225 | 58.4612 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 67.4225 | 1199.2765 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 58.4612 | 1190.3152 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 43.8906 | 1175.7446 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 17.5639 | 1149.4179
[5 empty] | 328 | 1133.338 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 65.1485 | 56.0971 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 65.1485 | 1198.4865 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 56.0971 | 1189.4351 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 41.3797 | 1174.7177 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 14.7866 | 1148.1246
[5 empty] | 330 | 1136.405 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 61.2916 | 52.15 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 61.2916 | 1197.6966 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 52.15 | 1188.555 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 37.2858 | 1173.6908 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 10.4263 | 1146.8313
[5 empty] | 332 | 1128.709 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 68.1976 | 58.9659 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 68.1976 | 1196.9066 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 58.9659 | 1187.6749 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 43.9549 | 1172.6639 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 16.829 | 1145.538
[5 empty] | 334 | 1120.713 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 75.4036 | 66.0818 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 75.4036 | 1196.1166 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 66.0818 | 1186.7948 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 50.924 | 1171.637 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 23.5317 | 1144.2447
[5 empty] | 336 | 1115.226 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 80.1007 | 70.6887 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 80.1007 | 1195.3267 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 70.6887 | 1185.9147 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 55.3841 | 1170.6101 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 27.7253 | 1142.9513
[5 empty] | 338 | 1108.709 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 85.8277 | 76.3256 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 85.8277 | 1194.5367 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 76.3256 | 1185.0346 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 60.8742 | 1169.5832 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 32.949 | 1141.658
[5 empty] | 340 | 1102.499 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 91.2477 | 81.6555 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 91.2477 | 1193.7467 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 81.6555 | 1184.1545 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 66.0573 | 1168.5563 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 37.8657 | 1140.3647
[5 empty] | 342 | 1096.349 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 96.6078 | 86.9255 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 96.6078 | 1192.9568 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 86.9255 | 1183.2745 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 71.1804 | 1167.5294 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 42.7224 | 1139.0714
[5 empty] | 344 | 1090.39 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 101.7768 | 92.0044 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 101.7768 | 1192.1668 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 92.0044 | 1182.3944 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 76.1125 | 1166.5025 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 47.388 | 1137.778
[5 empty] | 346 | 1087.765 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 103.6118 | 93.7493 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 103.6118 | 1191.3768 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 93.7493 | 1181.5143 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 77.7106 | 1165.4756 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 48.7197 | 1136.4847
[5 empty] | 348 | 1084.661 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 105.9259 | 95.9732 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 105.9259 | 1190.5869 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 95.9732 | 1180.6342 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 79.7877 | 1164.4487 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 50.5304 | 1135.1914
[5 empty] | 350 | 1081.662 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 108.1349 | 98.0921 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 108.1349 | 1189.7969 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 98.0921 | 1179.7541 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 81.7598 | 1163.4218 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 52.2361 | 1133.8981
[5 empty] | 352 | 1076.872 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 112.1349 | 102.002 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 112.1349 | 1189.0069 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 102.002 | 1178.874 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 85.5229 | 1162.3949 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 55.7327 | 1132.6047
[5 empty] | 354 | 1070.898 | 2 | 2 | 4.0831 | 1.2997 | 2300341.0533 | Greater Dynamic Pressures | 117.319 | 107.0959 | 12.5 | 1225368.3971 | 0.0085985 | 0.74029 | 0.049671 | 0.78997 | 0 | 117.319 | 1188.217 | 0.0096454 | 0.83043 | 0.049671 | 0.8801 | 0 | 107.0959 | 1177.9939 | 0.01135 | 0.97723 | 0.049671 | 1.0269 | 0 | 90.47 | 1161.368 | 0.014387 | 1.2437 | 0.049671 | 1.2933 | 0 | 60.4134 | 1131.3114
[5 empty] | 356 | 1065.018 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 121.848 | 111.4682 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 121.848 | 1186.866 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 111.4682 | 1176.4862 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 94.5866 | 1159.6046 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 64.0634 | 1129.0814
[5 empty] | 358 | 1059.58 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 125.9351 | 115.3985 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 125.9351 | 1185.5151 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 115.3985 | 1174.9785 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 98.2612 | 1157.8412 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 67.2714 | 1126.8514
[5 empty] | 360 | 1055.284 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 128.8801 | 118.1868 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 128.8801 | 1184.1641 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 118.1868 | 1173.4708 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 100.7938 | 1156.0778 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 69.3374 | 1124.6214
[5 empty] | 362 | 1050.886 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 131.9272 | 121.0772 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 131.9272 | 1182.8132 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 121.0772 | 1171.9632 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 103.4284 | 1154.3144 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 71.5054 | 1122.3914
[5 empty] | 364 | 1052.647 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 128.8152 | 117.8085 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 128.8152 | 1181.4622 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 117.8085 | 1170.4555 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 99.904 | 1152.551 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 67.5143 | 1120.1613
[5 empty] | 366 | 1051.117 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 128.9943 | 117.8308 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 128.9943 | 1180.1113 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 117.8308 | 1168.9478 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 99.6706 | 1150.7876 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 66.8143 | 1117.9313
[5 empty] | 368 | 1048.266 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 130.4943 | 119.1742 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 130.4943 | 1178.7603 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 119.1742 | 1167.4402 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 100.7582 | 1149.0242 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 67.4353 | 1115.7013
[5 empty] | 370 | 1040.172 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 137.2373 | 125.7605 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 137.2373 | 1177.4093 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 125.7605 | 1165.9325 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 107.0888 | 1147.2608 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 73.2993 | 1113.4713
[5 empty] | 372 | 1033.483 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 142.5754 | 130.9418 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 142.5754 | 1176.0584 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 130.9418 | 1164.4248 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 112.0144 | 1145.4974 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 77.7583 | 1111.2413
[5 empty] | 374 | 1030.95 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 143.7574 | 131.9672 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 143.7574 | 1174.7074 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 131.9672 | 1162.9172 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 112.784 | 1143.734 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 78.0613 | 1109.0113
[5 empty] | 376 | 1032.263 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 141.0935 | 129.1465 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 141.0935 | 1173.3565 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 129.1465 | 1161.4095 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 109.7076 | 1141.9706 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 74.5182 | 1106.7812
[5 empty] | 378 | 1031.391 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 140.6145 | 128.5108 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 140.6145 | 1172.0055 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 128.5108 | 1159.9018 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 108.8162 | 1140.2072 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 73.1602 | 1104.5512
[5 empty] | 380 | 1025.791 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 144.8636 | 132.6032 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 144.8636 | 1170.6546 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 132.6032 | 1158.3942 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 112.6528 | 1138.4438 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 76.5302 | 1102.3212
[5 empty] | 382 | 1020.911 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 148.3926 | 135.9755 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 148.3926 | 1169.3036 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 135.9755 | 1156.8865 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 115.7694 | 1136.6804 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 79.1802 | 1100.0912
[5 empty] | 384 | 1015.65 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 152.3027 | 139.7288 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 152.3027 | 1167.9527 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 139.7288 | 1155.3788 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 119.267 | 1134.917 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 82.2112 | 1097.8612
[5 empty] | 386 | 1012.139 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 154.4627 | 141.7321 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 154.4627 | 1166.6017 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 141.7321 | 1153.8711 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 121.0146 | 1133.1536 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 83.4922 | 1095.6312
[5 empty] | 388 | 1010.472 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 154.7788 | 141.8915 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 154.7788 | 1165.2508 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 141.8915 | 1152.3635 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 120.9182 | 1131.3902 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 82.9291 | 1093.4011
[5 empty] | 390 | 1005.401 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 158.4988 | 145.4548 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 158.4988 | 1163.8998 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 145.4548 | 1150.8558 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 124.2258 | 1129.6268 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 85.7701 | 1091.1711
[5 empty] | 392 | 996.666 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 165.8829 | 152.6821 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 165.8829 | 1162.5489 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 152.6821 | 1149.3481 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 131.1975 | 1127.8635 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 92.2751 | 1088.9411
[5 empty] | 394 | 991.35 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 169.8479 | 156.4905 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 169.8479 | 1161.1979 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 156.4905 | 1147.8405 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 134.7501 | 1126.1001 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 95.3611 | 1086.7111
[5 empty] | 396 | 990.486 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 169.361 | 155.8468 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 169.361 | 1159.847 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 155.8468 | 1146.3328 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 133.8507 | 1124.3367 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 93.9951 | 1084.4811
[5 empty] | 398 | 992.761 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 165.735 | 152.0641 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 165.735 | 1158.496 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 152.0641 | 1144.8251 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 129.8123 | 1122.5733 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 89.4901 | 1082.2511
[5 empty] | 400 | 999.077 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 158.068 | 144.2405 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 158.068 | 1157.145 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 144.2405 | 1143.3175 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 121.7329 | 1120.8099 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 80.944 | 1080.021
[5 empty] | 402 | 1001.8 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 153.9941 | 140.0098 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 153.9941 | 1155.7941 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 140.0098 | 1141.8098 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 117.2465 | 1119.0465 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 75.991 | 1077.791
[5 empty] | 404 | 1002.224 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 152.2191 | 138.0781 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 152.2191 | 1154.4431 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 138.0781 | 1140.3021 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 115.0591 | 1117.2831 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 73.337 | 1075.561
[5 empty] | 406 | 1002.003 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 151.0892 | 136.7915 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 151.0892 | 1153.0922 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 136.7915 | 1138.7945 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 113.5167 | 1115.5197 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 71.328 | 1073.331
[5 empty] | 408 | 1003.596 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 148.1452 | 133.6908 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 148.1452 | 1151.7412 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 133.6908 | 1137.2868 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 110.1603 | 1113.7563 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 67.505 | 1071.101
[5 empty] | 410 | 994.111 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 156.2793 | 141.6681 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 156.2793 | 1150.3903 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 141.6681 | 1135.7791 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 117.8819 | 1111.9929 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 74.76 | 1068.871
[5 empty] | 412 | 983.925 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 165.1143 | 150.3464 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 165.1143 | 1149.0393 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 150.3464 | 1134.2714 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 126.3045 | 1110.2295 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 82.7159 | 1066.6409
[5 empty] | 414 | 972.347 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 175.3414 | 160.4168 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 175.3414 | 1147.6884 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 160.4168 | 1132.7638 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 136.1191 | 1108.4661 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 92.0639 | 1064.4109
[5 empty] | 416 | 963.901 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 182.4364 | 167.3551 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 182.4364 | 1146.3374 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 167.3551 | 1131.2561 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 142.8017 | 1106.7027 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 98.2799 | 1062.1809
[5 empty] | 418 | 963.258 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 181.7285 | 166.4904 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 181.7285 | 1144.9865 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 166.4904 | 1129.7484 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 141.6813 | 1104.9393 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 96.6929 | 1059.9509
[5 empty] | 420 | 965.836 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 177.7995 | 162.4048 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 177.7995 | 1143.6355 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 162.4048 | 1128.2408 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 137.3399 | 1103.1759 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 91.8849 | 1057.7209
[5 empty] | 422 | 966.309 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 175.9756 | 160.4241 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 175.9756 | 1142.2846 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 160.4241 | 1126.7331 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 135.1035 | 1101.4125 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 89.1819 | 1055.4909
[5 empty] | 424 | 972.884 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 168.0496 | 152.3414 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 168.0496 | 1140.9336 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 152.3414 | 1125.2254 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 126.7651 | 1099.6491 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 80.3768 | 1053.2608
[5 empty] | 426 | 983.972 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 155.6106 | 139.7458 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 155.6106 | 1139.5826 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 139.7458 | 1123.7178 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 113.9137 | 1097.8857 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 67.0588 | 1051.0308
[5 empty] | 428 | 994.096 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 144.1357 | 128.1141 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 144.1357 | 1138.2317 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 128.1141 | 1122.2101 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 102.0263 | 1096.1223 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 54.7048 | 1048.8008
[5 empty] | 430 | 991.695 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 145.1857 | 129.0074 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 145.1857 | 1136.8807 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 129.0074 | 1120.7024 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 102.6639 | 1094.3589 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 54.8758 | 1046.5708
[5 empty] | 432 | 984.933 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 150.5968 | 134.2618 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 150.5968 | 1135.5298 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 134.2618 | 1119.1948 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 107.6625 | 1092.5955 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 59.4078 | 1044.3408
[5 empty] | 434 | 978.185 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 155.9938 | 139.5021 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 155.9938 | 1134.1788 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 139.5021 | 1117.6871 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 112.6471 | 1090.8321 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 63.9258 | 1042.1108
[5 empty] | 436 | 972.686 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 160.1419 | 143.4934 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 160.1419 | 1132.8279 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 143.4934 | 1116.1794 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 116.3827 | 1089.0687 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 67.1947 | 1039.8807
[5 empty] | 438 | 966.824 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 164.6529 | 147.8477 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 164.6529 | 1131.4769 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 147.8477 | 1114.6717 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 120.4813 | 1087.3053 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 70.8267 | 1037.6507
[5 empty] | 440 | 960.902 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 169.224 | 152.2621 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 169.224 | 1130.126 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 152.2621 | 1113.1641 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 124.6399 | 1085.5419 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 74.5187 | 1035.4207
[5 empty] | 442 | 952.924 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 175.851 | 158.7324 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 175.851 | 1128.775 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 158.7324 | 1111.6564 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 130.8545 | 1083.7785 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 80.2667 | 1033.1907
[5 empty] | 444 | 945.683 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 181.7411 | 164.4657 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 181.7411 | 1127.4241 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 164.4657 | 1110.1487 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 136.3321 | 1082.0151 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 85.2777 | 1030.9607
[5 empty] | 446 | 941.042 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 185.0311 | 167.5991 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 185.0311 | 1126.0731 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 167.5991 | 1108.6411 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 139.2097 | 1080.2517 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 87.6887 | 1028.7307
[5 empty] | 448 | 937.104 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 187.6182 | 170.0294 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 187.6182 | 1124.7222 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 170.0294 | 1107.1334 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 141.3843 | 1078.4883 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 89.3966 | 1026.5006
[5 empty] | 450 | 939.943 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 183.4282 | 165.6827 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 183.4282 | 1123.3712 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 165.6827 | 1105.6257 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 136.7819 | 1076.7249 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 84.3276 | 1024.2706
[5 empty] | 452 | 944.776 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 177.2442 | 159.3421 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 177.2442 | 1122.0202 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 159.3421 | 1104.1181 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 130.1855 | 1074.9615 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 77.2646 | 1022.0406
[5 empty] | 454 | 947.762 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 172.9073 | 154.8484 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 172.9073 | 1120.6693 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 154.8484 | 1102.6104 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 125.4362 | 1073.1982 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 72.0486 | 1019.8106
[5 empty] | 456 | 952.649 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 166.6693 | 148.4537 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 166.6693 | 1119.3183 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 148.4537 | 1101.1027 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 118.7858 | 1071.4348 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 64.9316 | 1017.5806
[5 empty] | 458 | 954.554 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 163.4134 | 145.0411 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 163.4134 | 1117.9674 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 145.0411 | 1099.5951 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 115.1174 | 1069.6714 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 60.7966 | 1015.3506
[5 empty] | 460 | 952.37 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 164.2464 | 145.7174 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 164.2464 | 1116.6164 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 145.7174 | 1098.0874 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 115.538 | 1067.908 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 60.7505 | 1013.1205
[5 empty] | 462 | 947.552 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 167.7135 | 149.0277 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 167.7135 | 1115.2655 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 149.0277 | 1096.5797 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 118.5926 | 1066.1446 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 63.3385 | 1010.8905
[5 empty] | 464 | 941.898 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 172.0165 | 153.174 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 172.0165 | 1113.9145 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 153.174 | 1095.072 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 122.4832 | 1064.3812 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 66.7625 | 1008.6605
[5 empty] | 466 | 940.521 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 172.0426 | 153.0434 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 172.0426 | 1112.5636 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 153.0434 | 1093.5644 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 122.0968 | 1062.6178 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 65.9095 | 1006.4305
[5 empty] | 468 | 939.702 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 171.5106 | 152.3547 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 171.5106 | 1111.2126 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 152.3547 | 1092.0567 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 121.1524 | 1060.8544 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 64.4985 | 1004.2005
[5 empty] | 470 | 937.147 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 172.7147 | 153.402 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 172.7147 | 1109.8617 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 153.402 | 1090.549 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 121.944 | 1059.091 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 64.8235 | 1001.9705
[5 empty] | 472 | 933.872 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 174.6387 | 155.1694 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 174.6387 | 1108.5107 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 155.1694 | 1089.0414 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 123.4556 | 1057.3276 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 65.8684 | 999.7404
[5 empty] | 474 | 933.184 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 173.9758 | 154.3497 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 173.9758 | 1107.1598 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 154.3497 | 1087.5337 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 122.3802 | 1055.5642 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 64.3264 | 997.5104
[5 empty] | 476 | 939.292 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 166.5168 | 146.734 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 166.5168 | 1105.8088 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 146.734 | 1086.026 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 114.5088 | 1053.8008 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 55.9884 | 995.2804
[5 empty] | 478 | 944.619 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 159.8388 | 139.8994 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 159.8388 | 1104.4578 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 139.8994 | 1084.5184 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 107.4184 | 1052.0374 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 48.4314 | 993.0504
[5 empty] | 480 | 954.023 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 149.0839 | 128.9877 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 149.0839 | 1103.1069 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 128.9877 | 1083.0107 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 96.251 | 1050.274 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 36.7974 | 990.8204
[5 empty] | 482 | 968.263 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 133.4929 | 113.24 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 133.4929 | 1101.7559 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 113.24 | 1081.503 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 80.2476 | 1048.5106 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 20.3274 | 988.5904
[5 empty] | 484 | 970.384 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 130.021 | 109.6114 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 130.021 | 1100.405 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 109.6114 | 1079.9954 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 76.3632 | 1046.7472 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 15.9763 | 986.3603
[5 empty] | 486 | 964.636 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 134.418 | 113.8517 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 134.418 | 1099.054 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 113.8517 | 1078.4877 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 80.3478 | 1044.9838 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 19.4943 | 984.1303
[5 empty] | 488 | 956.631 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 141.0721 | 120.349 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 141.0721 | 1097.7031 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 120.349 | 1076.98 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 86.5894 | 1043.2204 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 25.2693 | 981.9003
[5 empty] | 490 | 947.426 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 148.9261 | 128.0463 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 148.9261 | 1096.3521 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 128.0463 | 1075.4723 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 94.031 | 1041.457 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 32.2443 | 979.6703
[5 empty] | 492 | 941.72 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 153.2812 | 132.2447 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 153.2812 | 1095.0012 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 132.2447 | 1073.9647 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 97.9736 | 1039.6936 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 35.7203 | 977.4403
[5 empty] | 494 | 935.985 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 157.6652 | 136.472 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 157.6652 | 1093.6502 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 136.472 | 1072.457 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 101.9452 | 1037.9302 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 39.2253 | 975.2103
[5 empty] | 496 | 930.475 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 161.8243 | 140.4743 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 161.8243 | 1092.2993 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 140.4743 | 1070.9493 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 105.6918 | 1036.1668 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 42.5053 | 972.9803
[5 empty] | 498 | 927.611 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 163.3373 | 141.8307 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 163.3373 | 1090.9483 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 141.8307 | 1069.4417 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 106.7924 | 1034.4034 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 43.1392 | 970.7502
[5 empty] | 500 | 931.256 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 158.3414 | 136.678 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 158.3414 | 1089.5974 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 136.678 | 1067.934 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 101.384 | 1032.64 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 37.2642 | 968.5202
[5 empty] | 502 | 920.044 | 2 | 1.8 | 4.0831 | 1.6046 | 2555934.5036 | Greater Dynamic Pressures | 168.2024 | 146.3823 | 11.25 | 992548.4016 | 0.0087463 | 1.2752 | 0.075706 | 1.351 | 0 | 168.2024 | 1088.2464 | 0.0098211 | 1.432 | 0.075706 | 1.5077 | 0 | 146.3823 | 1066.4263 | 0.011575 | 1.6877 | 0.075706 | 1.7634 | 0 | 110.8326 | 1030.8766 | 0.01471 | 2.1543 | 0.075706 | 2.23 | 0 | 46.2462 | 966.2902
[5 empty] | 504 | 911.78 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 173.0401 | 150.8116 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 173.0401 | 1084.8201 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 150.8116 | 1062.5916 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 114.5933 | 1026.3733 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 48.7745 | 960.5545
[5 empty] | 506 | 907.989 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | Greater Dynamic Pressures | 173.4047 | 150.7679 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 173.4047 | 1081.3937 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 150.7679 | 1058.7569 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 113.8809 | 1021.8699 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 46.8299 | 954.8189
[5 empty] | 508 | 907.289 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 171.729 | 170.6784 | 171.729 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 170.6784 | 1077.9674 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 147.6332 | 1054.9222 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 110.0776 | 1017.3666 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 41.7942 | 949.0832
[5 empty] | 510 | 900.577 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 178.441 | 173.9641 | 178.441 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 173.9641 | 1074.5411 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 150.5105 | 1051.0875 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 112.2863 | 1012.8633 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 42.7706 | 943.3476
[5 empty] | 512 | 902.112 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 176.906 | 169.0027 | 176.906 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 169.0027 | 1071.1147 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 145.1408 | 1047.2528 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 106.2479 | 1008.3599 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 35.4999 | 937.6119
[5 empty] | 514 | 900.179 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 178.839 | 167.5094 | 178.839 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 167.5094 | 1067.6884 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 143.2391 | 1043.4181 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 103.6776 | 1003.8566 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 31.6973 | 931.8763
[5 empty] | 516 | 903.811 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 175.207 | 160.4511 | 175.207 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 160.4511 | 1064.2621 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 135.7725 | 1039.5835 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 95.5422 | 999.3532 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 22.3296 | 926.1406
[5 empty] | 518 | 910.027 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 168.991 | 150.8088 | 168.991 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 150.8088 | 1060.8358 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 125.7218 | 1035.7488 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 84.8229 | 994.8499 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 10.3779 | 920.4049
|  |  |  | Reservoir | 520 | 911.131 | 2 | 1.5 | 4.0831 | 2.3106 | 3067121.4044 | 10 | 10 | 10 | 9.375 | 689269.7233 | 0.0090113 | 3.2693 | 0.15698 | 3.4263 | 0 | 10 | 921.131 | 0.010137 | 3.6777 | 0.15698 | 3.8347 | 0 | 10 | 921.131 | 0.01198 | 4.3464 | 0.15698 | 4.5033 | 0 | 10 | 921.131 | 0.015294 | 5.5787 | 0.15698 | 5.7357 | 0 | 10 | 921.131
[13 empty] | 1057.4094 |  | Total Steel Mass (kg): | 407524002.8751 | [5 empty] | 1057.4094 | [6 empty] | 1031.9141 | [6 empty] | 990.3466 | [6 empty] | 914.6693
[13 empty] | 146.2784 | [8 empty] | 146.2784 | [6 empty] | 120.7831 | [6 empty] | 79.2156 | [6 empty] | 3.5383